## 1
1 | Building Summary Strip Mall pre-1980 construction
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 2090 | 2090 | 2090
nFloor |  | Number of Floors | 1 | 1 | 1
glazing |  | Glazing (Total) | 0.52 | 0.52 | 0.52
hCeiling |  | Floor to Ceiling Height (m) | 6 | 6 | 6
areaWall |  | Gross Dimensions - Total Area (m2) | 1184.13 | 1184.13 | 1184.13
ver2hor |  | Wall to Skin Ratio | 0.36 | 0.36 | 0.36
areaRoof |  | Gross Dimensions - Total Area (m2) | 2090 | 2090 | 2090
areaWindow |  | Total Window Area (m2) | 124 | 124 | 124

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD14PRE | Total | Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 107.1959 | 10 | 12.4789 | 0 | 0 | 10 | 0.3 | 3135.4806 |  | 0.33
BLD14PST | Total | Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 107.1959 | 10 | 12.4789 | 0 | 0 | 10 | 0.3 | 3135.4806 |  | 0.33
BLD14NEW | Total | Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 107.1959 | 10 | 12.4789 | 0 | 0 | 10 | 0.3 | 3135.4806 |  | 0.33
19.5

## 3
3 |  | Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD14PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD14PRE | TypeWall |  | Construction Type | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame
BLD14PRE | RvalWall |  | R-value (m2·K / W) | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
BLD14PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD14PRE | RvalRoof |  | R-value (m2·K / W) | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD14PRE | Uwindow |  | U-Factor (W / m2·K) | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41
BLD14PRE | SHGC |  | SHGC | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
BLD14PRE | HVAC |  | Air Conditioning (kW) | 350.4229 | 367.7293 | 362.344 | 359.0368 | 254.7724 | 307.7423 | 193.9309 | 338.9577 | 237.8199 | 216.9892 | 350.0232 | 251.382 | 391.4083 | 286.0778 | 404.949 | 383.7105
BLD14PRE | HEAT |  | Heating (kW) | 128.8817 | 266.7039 | 202.9248 | 323.7257 | 156.9328 | 254.3231 | 201.0967 | 371.3452 | 300.8821 | 285.5251 | 474.6292 | 391.9993 | 534.2325 | 501.9435 | 562.4258 | 765.2177
BLD14PRE | COP |  | Air Conditioning (COP) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
BLD14PRE | EffHeat |  | Heating Efficiency (%) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.79632 | 0.8 | 0.8 | 0.79318 | 0.79631 | 0.79318 | 0.79318 | 0.79318 | 0.79108
BLD14PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 14.32 | 15.05 | 15.93 | 15.23 | 12.89 | 15.37 | 11.38 | 13.96 | 13.99 | 12.25 | 14.32 | 14.37 | 16.09 | 17.07 | 17.38 | 23.18
BLD14PST | TypeWall |  | Construction Type | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame
BLD14PST | RvalWall |  | R-value (m2·K / W) | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
BLD14PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD14PST | RvalRoof |  | R-value (m2·K / W) | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD14PST | Uwindow |  | U-Factor (W / m2·K) | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41
BLD14PST | SHGC |  | SHGC | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
BLD14PST | HVAC |  | Air Conditioning (kW) | 357.7031 | 308.7502 | 297.8584 | 303.8614 | 248.8733 | 249.8526 | 166.5438 | 271.9175 | 196.6042 | 182.752 | 322.7438 | 232.8727 | 344.5217 | 268.1293 | 376.3603 | 348.7299
BLD14PST | HEAT |  | Heating (kW) | 134.2623 | 248.6001 | 190.213 | 299.5607 | 156.3269 | 232.453 | 189.2828 | 343.0383 | 275.744 | 266.7586 | 450.809 | 365.6892 | 506.6137 | 477.6924 | 530.1546 | 717.3636
BLD14PST | COP |  | Air Conditioning (COP) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
BLD14PST | EffHeat |  | Heating Efficiency (%) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.79319 | 0.79635 | 0.79319 | 0.79319 | 0.79319 | 0.79113
BLD14PST | Fan |  | Fan Max Flow Rate (m3/s ) | 14.93 | 12.49 | 12.67 | 12.55 | 12.52 | 11.63 | 9.6 | 11.22 | 11.24 | 9.93 | 13.26 | 12.85 | 14.92 | 15.88 | 15.9 | 21.06
BLD14NEW | TypeWall |  | Construction Type | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame | Steel-frame
BLD14NEW | RvalWall |  | R-value (m2·K / W) | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
BLD14NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD14NEW | RvalRoof |  | R-value (m2·K / W) | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD14NEW | Uwindow |  | U-Factor (W / m2·K) | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41
BLD14NEW | SHGC |  | SHGC | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
BLD14NEW | HVAC |  | Air Conditioning (kW) | 194.5732 | 198.0517 | 190.8755 | 193.9599 | 148.3206 | 168.9427 | 108.6552 | 186.4162 | 135.2865 | 121.9008 | 174.3013 | 126.3008 | 172.4897 | 116.4107 | 156.1244 | 132.2385
BLD14NEW | HEAT |  | Heating (kW) | 123.0115 | 163.3658 | 137.0094 | 180.2579 | 127.9373 | 150.1105 | 141.4129 | 209.0666 | 170.5872 | 171.1758 | 268.6911 | 223.1061 | 307.4366 | 291.6122 | 320.3789 | 420.4533
BLD14NEW | COP |  | Air Conditioning (COP) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
BLD14NEW | EffHeat |  | Heating Efficiency (%) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.79325
BLD14NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 7.85 | 7.97 | 7.71 | 7.82 | 6.68 | 7.15 | 5.88 | 7.5 | 7.36 | 6.18 | 7 | 6.75 | 6.95 | 6.8 | 6.36 | 7.97
2.53

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
| Sat |  |  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
| Sun |  |  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
| Sat |  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
| Sun |  |  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 43.5 | 2268.21
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 630 | 4428 | 230888.57
| Sat |  |  |  | Sat | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 624
| Sun |  |  |  | Sun, Hol, Other | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 654
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 455.4 | 2737.8 | 142756.71
| Sat |  |  |  | Sat | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 460.8
| Sun |  |  |  | Other | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 23.356 | 433.8
SchGas | WD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sat |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchSWH | WD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sat |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## BuildingSummary
1 | Building Summary Strip Mall pre-1980 construction
UWG |  |  | Value | Value | Value
Program
|  | Building Name | Strip Mall Reference Building pre-1980 construction | Strip Mall Reference Building post-1980 construction | Strip Mall Reference Building new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Strip Mall | Strip Mall | Strip Mall
Form
areaFloor |  | Total Floor Area (m2) | 2090 | 2090 | 2090
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 4 | 4 | 4
nFloor |  | Number of Floors | 1 | 1 | 1
|  | Window Fraction (Window to Wall Ratio) | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105 | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105 | South: 0.26 East: 0.00 North: 0.00 West: 0.00 Total: 0.105
glazing |  | Glazing (Total) | 0.105 | 0.105 | 0.105
|  | Skylight/TDD Percentage | 0.00%
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | 10 stores | 10 stores | 10 stores
hCeiling |  | Floor to Ceiling Height (m) | 5.1816 | 5.1816 | 5.1816
|  | Roof type | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Steel-frame | Steel-frame | Steel-frame
areaWall |  | Gross Dimensions - Total Area (m2) | 1184.13 | 1184.13 | 1184.13
|  | Net Dimensions - Total Area (m2) | 1059.67 | 1059.67 | 1059.67
ver2hor |  | Wall to Skin Ratio | 0.36 | 0.36 | 0.36
Roof
|  | Construction Type | IEAD | IEAD | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 2090 | 2090 | 2090
|  | Net Dimensions - Total Area (m2) | 2090 | 2090 | 2090
|  | Roof to Skin Ratio | 0.64 | 0.64 | 0.64
Window
|  | Dimensions - Total Area (m2) | South: 124 East: 0.00 North: 0.00 West: 0.00 Total: 124 | South: 124 East: 0.00 North: 0.00 West: 0.00 Total: 124 | South: 124 East: 0.00 North: 0.00 West: 0.00 Total: 124
areaWindow |  | Total Window Area (m2) | 124 | 124 | 124
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) | 0 | 0 | 0
|  | Operable area (m2) | 0 | 0 | 0
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
|  | Dimensions - Total Area (m2) | 2090 | 2090 | 2090
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 46.47 | 46.47 | 46.47
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 1.23 | 1.23 | 0.33
HVAC
|  | System Type | PSZ-AC | PSZ-AC | PSZ-AC
|  | Heating Type | Gas furnace | Gas furnace | Gas furnace
|  | Cooling Type | Unitary DX | Unitary DX | Unitary DX
|  | Fan Control | Constant volume | Constant volume | Constant volume
Service Water Heating
|  | SWH Type | N/A | N/A | N/A
|  | Fuel | N/A | N/A | N/A
|  | Thermal Efficiency (%) | N/A | N/A | N/A
|  | Temperature Setpoint (ºC ) | N/A | N/A | N/A
|  | Water Consumption (m3 ) | N/A | N/A | N/A

## ZoneSummary
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
|  | LGStore1 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 276.3003 | 20.75 | 6.1939 | 56.2472 | 60.2778 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.4124
|  | SMStore1 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 60.2778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore2 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore3 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore4 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | LGStore2 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 157.8901 | 20.75 | 6.1939 | 56.2472 | 29.0625 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.1446
|  | SMStore5 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore6 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore7 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore8 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 197.3602 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.6801
BLD14PRE | Total | Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 337.4831 | 38.4809 | 4.3056 | 0 |  |  | 1.5 | 3135.4806 |  | 1.2339
|  | LGStore1 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 276.3003 | 20.75 | 6.1939 | 56.2472 | 60.2778 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.4124
|  | SMStore1 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 60.2778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore2 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore3 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore4 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 35.5209 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | LGStore2 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 157.8901 | 20.75 | 6.1939 | 56.2472 | 29.0625 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 1.1446
|  | SMStore5 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore6 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore7 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.1446
|  | SMStore8 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 197.3602 | 10.37 | 6.1939 | 28.1236 | 29.0625 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 1.6801
BLD14PST | Total | Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 337.4831 | 38.4809 | 4.3056 | 0 |  |  | 1.5 | 3135.4806 |  | 1.2339
|  | LGStore1 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 276.3003 | 20.75 | 6.1939 | 56.2472 | 24.0035 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 0.37663
|  | SMStore1 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 24.0035 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 0.30523
|  | SMStore2 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 18.2986 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 0.30523
|  | SMStore3 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 18.2986 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 0.30523
|  | SMStore4 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 18.2986 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 0.30523
|  | LGStore2 | Yes | 1 | 348.3867 | 1805.1988 | 5.1816 | 157.8901 | 20.75 | 6.1939 | 56.2472 | 13.7778 | 4.3056 |  |  |  | 1.5 | 522.5801 |  | 0.30524
|  | SMStore5 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 13.7778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 0.30523
|  | SMStore6 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 13.7778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 0.30523
|  | SMStore7 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 78.9401 | 10.37 | 6.1939 | 28.1236 | 13.7778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 0.30523
|  | SMStore8 | Yes | 1 | 174.1934 | 902.5994 | 5.1816 | 197.3602 | 10.37 | 6.1939 | 28.1236 | 13.7778 | 4.3056 |  |  |  | 1.5 | 261.2901 |  | 0.44802
BLD14NEW | Total | Total Conditioned Zones |  |  | 2090.3204 | 10831.1928 |  | 1184.1311 | 124.4601 |  | 337.4831 | 17.4644 | 4.3056 | 0 |  |  | 1.5 | 3135.4806 |  | 0.32903

## LocationSummary
3 |  | Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD14PRE |  | Program
BLD14PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD14PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD14PRE |  |  | Weighting Factor
BLD14PRE |  | Fabric
BLD14PRE |  |  | Exterior walls
BLD14PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD14PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD14PRE |  |  | Roof
BLD14PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD14PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD14PRE |  |  | Window
BLD14PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD14PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD14PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD14PRE |  |  | Skylights/TDD
BLD14PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14PRE |  |  | Foundation
BLD14PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD14PRE |  |  | Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
BLD14PRE |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD14PRE |  | HVAC
BLD14PRE |  |  | HVAC Sizing
BLD14PRE | HVAC |  | Air Conditioning (kW) | 350.4229 | 367.7293 | 362.344 | 359.0368 | 254.7724 | 307.7423 | 193.9309 | 338.9577 | 237.8199 | 216.9892 | 350.0232 | 251.382 | 391.4083 | 286.0778 | 404.949 | 383.7105
BLD14PRE |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 30.9803 | 32.3126 | 32.438 | 31.5112 | 21.013 | 26.9703 | 15.362 | 31.495 | 21.7683 | 17.8756 | 40.8969 | 29.5495 | 46.3818 | 33.3184 | 48.9854 | 43.93
BLD14PRE |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 73.8427 | 76.2321 | 73.2524 | 71.4304 | 52.3588 | 64.0233 | 41.923 | 68.2765 | 51.0503 | 44.9519 | 63.4629 | 45.5097 | 70.5788 | 54.3582 | 69.1267 | 73.3031
BLD14PRE |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 34.5586 | 35.7226 | 33.5169 | 33.7026 | 24.976 | 28.9065 | 19.6738 | 32.6218 | 23.8441 | 21.6966 | 30.0252 | 21.1122 | 29.2497 | 21.833 | 28.782 | 29.709
BLD14PRE |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 28.4115 | 29.9863 | 29.2042 | 29.2568 | 20.9105 | 24.7341 | 15.8663 | 27.8845 | 18.9029 | 17.813 | 26.9735 | 18.9483 | 30.6689 | 21.7377 | 31.2923 | 29.6142
BLD14PRE |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 27.7903 | 29.3604 | 28.79 | 28.8353 | 20.5213 | 24.3282 | 15.4941 | 27.2462 | 18.5008 | 17.4337 | 26.9681 | 19.0944 | 30.6632 | 21.8053 | 31.6242 | 29.6103
BLD14PRE |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 27.6947 | 29.2641 | 28.7223 | 28.7691 | 20.4558 | 24.2568 | 15.4224 | 27.1405 | 18.4223 | 17.3647 | 26.9862 | 19.1426 | 30.6823 | 21.7728 | 31.7173 | 29.627
BLD14PRE |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 49.619 | 52.6564 | 53.8555 | 53.0224 | 36.6863 | 45.2666 | 27.2112 | 48.5213 | 33.5889 | 31.0885 | 53.591 | 39.1953 | 60.9668 | 44.542 | 64.8996 | 58.9191
BLD14PRE |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 25.8629 | 27.4162 | 27.5176 | 27.515 | 19.3106 | 23.0893 | 14.355 | 25.2886 | 17.2735 | 16.2795 | 26.9867 | 19.5532 | 30.6829 | 22.1839 | 32.7606 | 29.6273
BLD14PRE |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 25.7553 | 27.3077 | 27.4511 | 27.4414 | 19.2426 | 23.0262 | 14.2954 | 25.1803 | 17.2106 | 16.2174 | 26.9781 | 19.571 | 30.6737 | 22.1985 | 32.8059 | 29.6175
BLD14PRE |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 25.9074 | 27.4708 | 27.5961 | 27.5528 | 19.2977 | 23.141 | 14.3279 | 25.3031 | 17.2581 | 16.2685 | 27.1547 | 19.7056 | 30.8602 | 22.3279 | 32.955 | 29.7532
BLD14PRE | HEAT |  | Heating (kW) | 128.8817 | 266.7039 | 202.9248 | 323.7257 | 156.9328 | 254.3231 | 201.0967 | 371.3452 | 300.8821 | 285.5251 | 474.6292 | 391.9993 | 534.2325 | 501.9435 | 562.4258 | 765.2177
BLD14PRE |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 13.618 | 28.6169 | 21.7163 | 34.6089 | 16.9735 | 27.1264 | 21.556 | 39.2256 | 31.9461 | 30.2112 | 50.1036 | 41.5663 | 56.3349 | 53.0426 | 59.1711 | 80.151
BLD14PRE |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 23.0051 | 49.3923 | 37.4889 | 59.8412 | 29.1387 | 46.9106 | 37.197 | 68.2958 | 55.4202 | 52.5446 | 87.3168 | 72.2322 | 98.2519 | 92.373 | 103.3305 | 140.3536
BLD14PRE |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 10.251 | 21.0526 | 16.0455 | 25.578 | 12.374 | 20.1245 | 15.8878 | 29.4134 | 23.8232 | 22.6123 | 37.5782 | 31.0213 | 42.2986 | 39.7328 | 44.5544 | 60.6606
BLD14PRE |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9671 | 15.9747 | 25.4784 | 12.3158 | 20.0395 | 15.8197 | 29.3186 | 23.7312 | 22.5344 | 37.4706 | 30.916 | 42.1853 | 39.6179 | 44.44 | 60.5309
BLD14PRE |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9628 | 15.9713 | 25.4737 | 12.3127 | 20.0357 | 15.8163 | 29.3143 | 23.727 | 22.5307 | 37.4657 | 30.9113 | 42.1802 | 39.6128 | 44.4349 | 60.5256
BLD14PRE |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9742 | 15.9826 | 25.4882 | 12.3205 | 20.0499 | 15.8262 | 29.3292 | 23.7426 | 22.5427 | 37.4821 | 30.9283 | 42.1974 | 39.631 | 44.4532 | 60.5483
BLD14PRE |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 41.6904 | 31.7016 | 50.6529 | 24.4501 | 39.7745 | 31.4187 | 58.3339 | 47.1447 | 44.8159 | 74.6201 | 61.5001 | 84.0391 | 78.8879 | 88.5322 | 120.6425
BLD14PRE |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9746 | 15.983 | 25.4887 | 12.3209 | 20.0503 | 15.8266 | 29.3296 | 23.743 | 22.5431 | 37.4826 | 30.9287 | 42.198 | 39.6316 | 44.4537 | 60.5489
BLD14PRE |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 10.251 | 20.9707 | 15.9776 | 25.4824 | 12.3184 | 20.0429 | 15.8226 | 29.3223 | 23.7347 | 22.5376 | 37.4747 | 30.92 | 42.1897 | 39.6222 | 44.4442 | 60.5354
BLD14PRE |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 10.251 | 21.1022 | 16.0833 | 25.6334 | 12.4081 | 20.1688 | 15.9259 | 29.4626 | 23.8694 | 22.6528 | 37.6348 | 31.075 | 42.3574 | 39.7918 | 44.6116 | 60.721
BLD14PRE |  |  | HVAC Efficiency
BLD14PRE | COP |  | Air Conditioning (COP) | 3.4148 | 3.4154 | 3.4157 | 3.4167 | 3.4589 | 3.429 | 3.5489 | 3.4311 | 3.534 | 3.552 | 3.4097 | 3.4895 | 3.3965 | 3.4309 | 3.4096 | 3.3948
BLD14PRE |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3
BLD14PRE |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.23 | 3.3 | 3.3 | 3.23
BLD14PRE |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PRE |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PRE |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PRE |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PRE |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.3
BLD14PRE |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PRE |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PRE |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PRE | EffHeat |  | Heating Efficiency (%) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.79632 | 0.8 | 0.8 | 0.79318 | 0.79631 | 0.79318 | 0.79318 | 0.79318 | 0.79108
BLD14PRE |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
BLD14PRE |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD14PRE |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PRE |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PRE |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PRE |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PRE |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
BLD14PRE |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PRE |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PRE |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PRE |  |  | HVAC Control - Economizer
BLD14PRE |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD14PRE |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD14PRE |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PRE |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PRE |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PRE |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PRE |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD14PRE |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PRE |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PRE |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 14.32 | 15.05 | 15.93 | 15.23 | 12.89 | 15.37 | 11.38 | 13.96 | 13.99 | 12.25 | 14.32 | 14.37 | 16.09 | 17.07 | 17.38 | 23.18
BLD14PRE |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 1.25 | 1.3 | 1.43 | 1.32 | 1.04 | 1.35 | 0.89 | 1.27 | 1.27 | 0.99 | 1.65 | 1.65 | 1.87 | 1.99 | 2.01 | 2.65
BLD14PRE |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 3.15 | 3.27 | 3.45 | 3.28 | 2.82 | 3.38 | 2.53 | 2.98 | 3.08 | 2.66 | 2.72 | 2.75 | 3.09 | 3.28 | 3.33 | 4.43
BLD14PRE |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 1.42 | 1.48 | 1.55 | 1.51 | 1.32 | 1.51 | 1.19 | 1.4 | 1.44 | 1.27 | 1.25 | 1.28 | 1.24 | 1.32 | 1.34 | 1.79
BLD14PRE |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 1.14 | 1.21 | 1.27 | 1.23 | 1.05 | 1.23 | 0.93 | 1.12 | 1.12 | 1 | 1.09 | 1.09 | 1.24 | 1.31 | 1.34 | 1.79
BLD14PRE |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 1.12 | 1.18 | 1.25 | 1.2 | 1.02 | 1.2 | 0.9 | 1.1 | 1.09 | 0.97 | 1.09 | 1.09 | 1.23 | 1.31 | 1.34 | 1.79
BLD14PRE |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 1.12 | 1.18 | 1.24 | 1.19 | 1.02 | 1.2 | 0.9 | 1.09 | 1.09 | 0.97 | 1.09 | 1.09 | 1.24 | 1.31 | 1.34 | 1.79
BLD14PRE |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 2 | 2.12 | 2.24 | 2.15 | 1.8 | 2.15 | 1.57 | 1.95 | 1.91 | 1.71 | 2.16 | 2.15 | 2.46 | 2.61 | 2.66 | 3.56
BLD14PRE |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 1.04 | 1.1 | 1.17 | 1.12 | 0.94 | 1.12 | 0.83 | 1.02 | 1 | 0.9 | 1.09 | 1.09 | 1.24 | 1.31 | 1.34 | 1.79
BLD14PRE |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 1.04 | 1.1 | 1.16 | 1.11 | 0.94 | 1.11 | 0.82 | 1.01 | 0.99 | 0.89 | 1.09 | 1.09 | 1.24 | 1.31 | 1.34 | 1.79
BLD14PRE |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 1.04 | 1.11 | 1.17 | 1.12 | 0.94 | 1.12 | 0.82 | 1.02 | 1 | 0.89 | 1.09 | 1.09 | 1.24 | 1.32 | 1.34 | 1.8
BLD14PRE |  | Utility Costs
BLD14PRE |  |  | Electric Utility Rates
BLD14PRE |  |  | Average Annual Rate ($/kWh) | 0.086087 | 0.11976 | 0.097996 | 0.099983 | 0.12942 | 0.099062 | 0.14786 | 0.075988 | 0.037294 | 0.074925 | 0.092417 | 0.037306 | 0.060239 | 0.074761 | 0.058902 | 0.094431
BLD14PRE |  |  | Total Cost ($/m2) | 26.9 | 35.17 | 29.79 | 26.88 | 30.77 | 27.87 | 33.28 | 19.41 | 9.38 | 17.12 | 22.89 | 9.08 | 15.09 | 18.35 | 14.43 | 26.1
BLD14PRE |  |  | Gas Utility Rates
BLD14PRE |  |  | Average Annual Rate ($/MJ) | 0.011404 | 0.0080433 | 0.0081453 | 0.0095079 | 0.0086121 | 0.0076307 | 0.0085682 | 0.0096568 | 0.0068715 | 0.0084173 | 0.0083015 | 0.0069072 | 0.0078698 | 0.008082 | 0.0078597 | 0.0041216
BLD14PRE |  |  | Total Cost ($/m2) | 0.11 | 1.25 | 1.02 | 3.11 | 0.82 | 1.63 | 2.3 | 5.63 | 2.84 | 4.4 | 6.7 | 4.18 | 8.28 | 6.97 | 10.39 | 8.87
BLD14PRE |  |  | Total Utility Costs
BLD14PRE |  |  | Cost Intensity ($/m2) | 27.01 | 36.42 | 30.8 | 29.98 | 31.6 | 29.5 | 35.58 | 25.04 | 12.22 | 21.52 | 29.59 | 13.26 | 23.36 | 25.32 | 24.82 | 34.96
BLD14PRE |  | Energy - End Uses
BLD14PRE |  |  | Electricity (kWh)
BLD14PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Cooling | 175338.8889 | 131333.3333 | 148088.8889 | 77658.3333 | 27708.3333 | 103183.3333 | 9591.6667 | 55858.3333 | 47636.1111 | 10913.8889 | 37227.7778 | 28011.1111 | 31197.2222 | 15508.3333 | 10622.2222 | 4530.5556
BLD14PRE |  |  | Interior Lighting | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500
BLD14PRE |  |  | Exterior Lighting | 59002.7778 | 58980.5556 | 58969.4444 | 58961.1111 | 58916.6667 | 58902.7778 | 58933.3333 | 58897.2222 | 58922.2222 | 58802.7778 | 58908.3333 | 58875 | 58869.4444 | 58855.5556 | 58822.2222 | 58461.1111
BLD14PRE |  |  | Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
BLD14PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Fans | 84797.2222 | 89569.4444 | 94300 | 91302.7778 | 76438.8889 | 92088.8889 | 67930.5556 | 85252.7778 | 84986.1111 | 73894.4444 | 87675 | 87850 | 99411.1111 | 104794.4444 | 108636.1111 | 180697.2222
BLD14PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total End Uses | 653116.6667 | 613861.1111 | 635336.1111 | 561902.7778 | 497044.4444 | 588152.7778 | 470433.3333 | 533988.8889 | 525522.2222 | 477588.8889 | 517788.8889 | 508713.8889 | 523458.3333 | 513136.1111 | 512058.3333 | 577666.6667
BLD14PRE |  |  | Gas (MJ)
BLD14PRE |  |  | Heating | 19780 | 324810 | 260910 | 683100 | 199290 | 446830 | 560800 | 1218690 | 864140 | 1091850 | 1687160 | 1266020 | 2198010 | 1802130 | 2762780 | 4496370
BLD14PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total End Uses | 19780 | 324810 | 260910 | 683100 | 199290 | 446830 | 560800 | 1218690 | 864140 | 1091850 | 1687160 | 1266020 | 2198010 | 1802130 | 2762780 | 4496370
BLD14PRE |  |  | Purchased Cooling (MJ)
BLD14PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Purchased Heating (MJ)
BLD14PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total Building (MJ) | 2371000 | 2534710 | 2548130 | 2705950 | 1988640 | 2564180 | 2254370 | 3141050 | 2756020 | 2811170 | 3551200 | 3097380 | 4082450 | 3649420 | 4606190 | 6575980
BLD14PRE |  | Energy - End Use Intensities
BLD14PRE |  |  | Electricity (MJ/m2)
BLD14PRE |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Cooling (elec) | 301.9729 | 226.1855 | 255.0423 | 133.7451 | 47.72 | 177.7048 | 16.519 | 96.2006 | 82.0401 | 18.7962 | 64.1146 | 48.2414 | 53.7286 | 26.7088 | 18.2938 | 7.8026
BLD14PRE |  |  | Interior Lighting (elec) | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506
BLD14PRE |  |  | Exterior Lighting (elec) | 101.616 | 101.5777 | 101.5586 | 101.5443 | 101.4677 | 101.4438 | 101.4964 | 101.4342 | 101.4773 | 101.2716 | 101.4534 | 101.396 | 101.3864 | 101.3625 | 101.3051 | 100.6831
BLD14PRE |  |  | Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
BLD14PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Fans (elec) | 146.0398 | 154.2587 | 162.4058 | 157.2439 | 131.6449 | 158.5977 | 116.9917 | 146.8244 | 146.3651 | 127.2628 | 150.996 | 151.2974 | 171.2082 | 180.4795 | 187.0958 | 311.2012
BLD14PRE |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total End Uses | 1124.8134 | 1057.2066 | 1094.1913 | 967.7226 | 856.022 | 1012.931 | 810.1917 | 919.6487 | 905.0672 | 822.5152 | 891.7486 | 876.1194 | 901.5127 | 883.7355 | 881.8793 | 994.8716
BLD14PRE |  |  | Gas (MJ/m2)
BLD14PRE |  |  | Heating (gas) | 9.4627 | 155.3877 | 124.8182 | 326.7921 | 95.3395 | 213.7615 | 268.2843 | 583.016 | 413.4008 | 522.3363 | 807.13 | 605.6585 | 1051.5184 | 862.1312 | 1321.7019 | 2151.0439
BLD14PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total End Uses | 9.4627 | 155.3877 | 124.8182 | 326.7921 | 95.3395 | 213.7615 | 268.2843 | 583.016 | 413.4008 | 522.3363 | 807.13 | 605.6585 | 1051.5184 | 862.1312 | 1321.7019 | 2151.0439
BLD14PRE |  |  | Purchased Cooling (MJ/m2)
BLD14PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Purchased Heating (MJ/m2)
BLD14PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total Building (MJ/m2) | 1134.2761 | 1212.5942 | 1219.0143 | 1294.5147 | 951.3567 | 1226.6926 | 1078.4808 | 1502.6647 | 1318.468 | 1344.8515 | 1698.8786 | 1481.7731 | 1953.0263 | 1745.8667 | 2203.5813 | 3145.9202
BLD14PRE |  | Peak Energy Demand
BLD14PRE |  |  | Electricity Peak Demand (kW)
BLD14PRE |  |  | Jan | 146.4296 | 137.4675 | 128.5554 | 115.9488 | 125.4999 | 113.2943 | 106.7425 | 109.6364 | 109.5999 | 107.7122 | 109.9543 | 110.0038 | 111.9292 | 113.0618 | 113.3822 | 125.6682
BLD14PRE |  |  | Feb | 155.01 | 142.3587 | 134.7534 | 118.9512 | 120.9268 | 118.9297 | 113.385 | 109.6364 | 114.3004 | 107.7122 | 109.9543 | 110.0038 | 111.9292 | 113.0618 | 113.3822 | 125.6682
BLD14PRE |  |  | Mar | 155.0151 | 144.1351 | 156.2069 | 128.0054 | 120.5303 | 124.1686 | 106.7425 | 121.4524 | 113.4483 | 107.7122 | 109.9543 | 112.336 | 111.9292 | 103.3422 | 113.3822 | 125.6682
BLD14PRE |  |  | Apr | 163.6167 | 166.276 | 160.2718 | 144.9836 | 129.443 | 153.2183 | 114.8637 | 122.5182 | 133.3187 | 108.8364 | 109.8726 | 119.2516 | 113.2294 | 100.3635 | 101.2038 | 112.1692
BLD14PRE |  |  | May | 176.0499 | 179.3385 | 186.1821 | 156.7498 | 122.9349 | 167.5619 | 116.7497 | 140.0049 | 138.5435 | 116.9684 | 137.0052 | 128.4062 | 166.1637 | 120.6703 | 117.5612 | 118.0433
BLD14PRE |  |  | Jun | 182.2519 | 181.6688 | 217.2938 | 172.0374 | 125.5448 | 202.7245 | 118.6235 | 175.6186 | 155.2779 | 122.2822 | 166.5044 | 143.0366 | 163.3483 | 148.8766 | 137.7782 | 140.6241
BLD14PRE |  |  | Jul | 176.1681 | 189.1064 | 212.3848 | 190.1971 | 132.7909 | 197.7232 | 129.2797 | 184.0885 | 161.6713 | 134.9634 | 170.204 | 151.5536 | 170.2303 | 149.6962 | 152.4175 | 147.7269
BLD14PRE |  |  | Aug | 184.8 | 189.2561 | 212.5324 | 178.381 | 143.6064 | 192.4067 | 125.2022 | 185.3312 | 158.2573 | 129.7611 | 165.5311 | 154.1379 | 161.1044 | 143.1437 | 152.9222 | 139.1753
BLD14PRE |  |  | Sep | 176.0174 | 184.0918 | 198.6788 | 165.3282 | 144.3959 | 186.9815 | 145.371 | 159.2994 | 141.9323 | 152.2117 | 143.5055 | 142.1518 | 139.9519 | 134.1554 | 128.0457 | 113.1762
BLD14PRE |  |  | Oct | 171.9372 | 162.0554 | 162.5822 | 152.6672 | 134.3684 | 155.2981 | 116.4426 | 137.5374 | 128.1626 | 107.7122 | 126.0914 | 128.6363 | 125.8115 | 115.9454 | 122.5854 | 125.6682
BLD14PRE |  |  | Nov | 157.8514 | 144.1388 | 147.8961 | 119.5027 | 127.6105 | 123.5888 | 106.7874 | 125.4302 | 114.9813 | 107.7365 | 124.1737 | 112.6711 | 112.2842 | 113.0618 | 113.3822 | 125.6682
BLD14PRE |  |  | Dec | 148.0486 | 140.5872 | 127.3265 | 113.3322 | 128.3246 | 120.1507 | 106.7425 | 109.6364 | 109.5999 | 107.7122 | 109.9543 | 110.0038 | 111.9292 | 113.0618 | 113.3822 | 125.6682
BLD14PRE |  |  | Time of Peak Electrical Demand
BLD14PRE |  |  | Jan | 24-JAN-13:00 | 03-JAN-13:00 | 28-JAN-17:00 | 23-JAN-17:00 | 26-JAN-13:50 | 18-JAN-16:49 | 02-JAN-16:00 | 02-JAN-16:49 | 02-JAN-17:10 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
BLD14PRE |  |  | Feb | 25-FEB-13:50 | 23-FEB-15:09 | 28-FEB-15:00 | 18-FEB-14:50 | 13-FEB-11:00 | 07-FEB-17:10 | 15-FEB-17:49 | 01-FEB-17:30 | 14-FEB-17:49 | 01-FEB-17:10 | 01-FEB-16:00 | 01-FEB-17:19 | 01-FEB-17:19 | 01-FEB-17:30 | 01-FEB-17:10 | 01-FEB-09:09
BLD14PRE |  |  | Mar | 13-MAR-14:00 | 25-MAR-12:39 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-14:09 | 31-MAR-14:39 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-17:00 | 01-MAR-17:49 | 01-MAR-17:40 | 30-MAR-15:00 | 01-MAR-17:00 | 30-MAR-16:00 | 01-MAR-17:49 | 01-MAR-17:00
BLD14PRE |  |  | Apr | 01-APR-14:39 | 29-APR-14:09 | 01-APR-15:50 | 15-APR-15:30 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 06-APR-16:00 | 04-APR-14:00 | 01-APR-09:09
BLD14PRE |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-15:09 | 15-MAY-14:00 | 30-MAY-12:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
BLD14PRE |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-14:50 | 29-JUN-14:09 | 28-JUN-14:50 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 20-JUN-16:00
BLD14PRE |  |  | Jul | 13-JUL-14:00 | 29-JUL-14:00 | 11-JUL-15:00 | 03-JUL-14:00 | 24-JUL-14:09 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-14:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-12:00 | 29-JUL-16:00
BLD14PRE |  |  | Aug | 21-AUG-14:20 | 31-AUG-14:09 | 01-AUG-14:00 | 17-AUG-13:00 | 08-AUG-12:00 | 05-AUG-12:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:09 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
BLD14PRE |  |  | Sep | 07-SEP-13:00 | 16-SEP-13:50 | 09-SEP-14:00 | 11-SEP-13:00 | 23-SEP-13:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 02-SEP-14:00 | 02-SEP-15:20 | 05-SEP-14:09 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 02-SEP-15:00
BLD14PRE |  |  | Oct | 06-OCT-14:20 | 12-OCT-14:00 | 24-OCT-14:50 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 13-OCT-14:50 | 20-OCT-14:39 | 13-OCT-14:00 | 26-OCT-16:00 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 23-OCT-08:09
BLD14PRE |  |  | Nov | 07-NOV-15:09 | 27-NOV-17:19 | 13-NOV-15:09 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-16:40 | 13-NOV-16:00 | 04-NOV-12:00 | 08-NOV-17:10 | 04-NOV-16:49 | 02-NOV-16:49 | 04-NOV-16:00 | 02-NOV-16:00 | 06-NOV-17:10 | 01-NOV-16:49 | 01-NOV-08:09
BLD14PRE |  |  | Dec | 16-DEC-12:00 | 02-DEC-17:19 | 09-DEC-17:19 | 01-DEC-17:30 | 19-DEC-12:00 | 05-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
BLD14PRE |  | Source Energy
BLD14PRE |  |  | Total Source Energy (GJ) | 7820.61 | 8381.06 | 7519.37 | 7550.8 | 5755.68 | 8061.69 | 5853.97 | 8205.16 | 7220.89 | 4187.36 | 8452.27 | 7458.97 | 8877.07 | 8389.11 | 9352.76 | 12338.38
BLD14PRE |  |  | Total Source Energy (MJ/m2) | 3741.35 | 4009.46 | 3597.24 | 3612.27 | 2753.5 | 3856.68 | 2800.52 | 3925.32 | 3454.45 | 2003.22 | 4043.53 | 3568.34 | 4246.76 | 4013.32 | 4474.32 | 5902.63
BLD14PRE |  | Water Consumption (m3)
BLD14PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  | Emissions
BLD14PRE |  |  | Carbon Equivalent (kg) | 179474.1025 | 210617.5011 | 196497.582 | 185404.4747 | 61681.0997 | 206426.5775 | 65090.4407 | 166075.8938 | 230257.3591 | 54473.8315 | 306483.1715 | 230638.0871 | 218811.9389 | 220016.6665 | 225094.4529 | 243630.0963
BLD14PRE |  |  | CO2 (kg) | 415786.5344 | 530724.8528 | 464631.9367 | 428426.2185 | 165466.4594 | 493119.2832 | 175998.8684 | 386642.046 | 545234.3137 | 139516.0244 | 724844.2487 | 550173.1401 | 527587.1197 | 530036.6395 | 548016.4837 | 641447.2626
BLD14PRE |  |  | NOX (kg) | 732.4016 | 690.7097 | 774.6692 | 790.878 | 142.1429 | 791.6379 | 152.1375 | 703.7482 | 918.516 | 184.4106 | 1239.6098 | 909.4542 | 857.7449 | 859.4408 | 868.0437 | 722.805
BLD14PRE |  |  | SO2 (kg) | 2795.6116 | 2928.2079 | 2554.8865 | 1972.4584 | 1446.3904 | 3235.4271 | 1369.0562 | 1949.596 | 2295.0793 | 369.4314 | 3489.9399 | 2221.7887 | 1236.0333 | 1370.6193 | 1209.28 | 2941.7631
BLD14PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PRE |  |  | Hg (kg) | 0.0127 | 0.0083 | 0.007 | 0.0073 | 0.0007 | 0.0061 | 0.0007 | 0.008 | 0.009 | 0.0016 | 0.0107 | 0.0088 | 0.0092 | 0.0097 | 0.0091 | 0.0104
BLD14PRE |  |  | Water for Electricity (m3) | 345.9945 | 998.8251 | 18872.3 | 3508.29 | 8726.97 | 16135.4 | 8259.76 | 121.2353 | 2386.29 | 4879.44 | 803.3196 | 2309.96 | 812.1135 | 32504.2 | 794.4279 | 590.1912
BLD14PST |  | Program
BLD14PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD14PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD14PST |  |  | Weighting Factor
BLD14PST |  | Fabric
BLD14PST |  |  | Exterior walls
BLD14PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD14PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD14PST |  |  | Roof
BLD14PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD14PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD14PST |  |  | Window
BLD14PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD14PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD14PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD14PST |  |  | Skylights/TDD
BLD14PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14PST |  |  | Foundation
BLD14PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD14PST |  |  | Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
BLD14PST |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD14PST |  | HVAC
BLD14PST |  |  | HVAC Sizing
BLD14PST | HVAC |  | Air Conditioning (kW) | 357.7031 | 308.7502 | 297.8584 | 303.8614 | 248.8733 | 249.8526 | 166.5438 | 271.9175 | 196.6042 | 182.752 | 322.7438 | 232.8727 | 344.5217 | 268.1293 | 376.3603 | 348.7299
BLD14PST |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 38.5949 | 26.1373 | 28.4239 | 25.9957 | 20.5005 | 21.7242 | 13.0774 | 27.6097 | 19.9367 | 16.2551 | 37.2093 | 27.5345 | 41.9609 | 31.0378 | 44.8493 | 39.3675
BLD14PST |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 83.331 | 67.4229 | 64.3683 | 62.6198 | 51.2514 | 53.0879 | 35.3736 | 58.1394 | 41.5959 | 37.6208 | 60.9154 | 40.367 | 57.7318 | 50.0428 | 67.2752 | 66.2267
BLD14PST |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 33.4639 | 31.6905 | 24.5271 | 30.1801 | 24.5021 | 24.4298 | 17.6378 | 24.6248 | 20.0359 | 18.9239 | 24.129 | 18.7732 | 24.4355 | 20.3744 | 20.5222 | 27.0733
BLD14PST |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 27.2467 | 24.9474 | 24.5818 | 25.21 | 20.4342 | 20.1425 | 13.8131 | 22.1868 | 15.713 | 15.0183 | 25.0788 | 17.7372 | 25.6148 | 20.4762 | 30.1405 | 27.0236
BLD14PST |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 26.6372 | 24.3143 | 23.9202 | 24.556 | 20.0427 | 19.7057 | 13.4259 | 21.5473 | 15.2497 | 14.619 | 25.0752 | 17.9067 | 26.1693 | 20.5099 | 30.5258 | 27.0216
BLD14PST |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 26.5415 | 24.2036 | 23.7908 | 24.4409 | 19.9747 | 19.6143 | 13.344 | 21.4291 | 15.161 | 14.5365 | 25.089 | 17.9582 | 26.3747 | 20.5537 | 30.5455 | 27.0326
BLD14PST |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 47.4863 | 43.0097 | 42.3259 | 43.3126 | 35.7678 | 35.9847 | 23.2167 | 37.6622 | 27.0658 | 25.6109 | 49.8874 | 36.9904 | 56.6841 | 42.0728 | 60.7862 | 53.8402
BLD14PST |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 24.755 | 22.371 | 21.9492 | 22.5502 | 18.8262 | 18.3955 | 12.2484 | 19.6155 | 13.9798 | 13.4159 | 25.0894 | 18.4927 | 28.4896 | 20.9848 | 30.5458 | 27.0328
BLD14PST |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 24.6631 | 22.2699 | 21.8638 | 22.4457 | 18.7597 | 18.3377 | 12.1917 | 19.5162 | 13.9192 | 13.3571 | 25.0817 | 18.5144 | 28.4812 | 21.0004 | 30.5367 | 27.0252
BLD14PST |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 24.9836 | 22.3834 | 22.1076 | 22.5504 | 18.8141 | 18.4302 | 12.2151 | 19.5865 | 13.9472 | 13.3946 | 25.1884 | 18.5985 | 28.5797 | 21.0763 | 30.633 | 27.0864
BLD14PST | HEAT |  | Heating (kW) | 134.2623 | 248.6001 | 190.213 | 299.5607 | 156.3269 | 232.453 | 189.2828 | 343.0383 | 275.744 | 266.7586 | 450.809 | 365.6892 | 506.6137 | 477.6924 | 530.1546 | 717.3636
BLD14PST |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 15.9982 | 26.3699 | 20.726 | 31.4867 | 16.8678 | 24.6744 | 19.8979 | 35.6436 | 28.795 | 27.7433 | 46.7607 | 38.0306 | 52.3582 | 49.4862 | 54.722 | 73.9084
BLD14PST |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 26.0055 | 45.8321 | 35.4647 | 54.9918 | 28.9946 | 42.8275 | 34.716 | 62.6765 | 50.4473 | 48.7378 | 82.3214 | 66.8201 | 92.3812 | 87.1698 | 96.625 | 130.6716
BLD14PST |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6647 | 14.9645 | 23.7484 | 12.3331 | 18.4002 | 15.0157 | 27.2555 | 21.9023 | 21.1977 | 35.8239 | 29.0568 | 40.2824 | 37.9746 | 42.1633 | 57.0552
BLD14PST |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6 | 14.8913 | 23.6794 | 12.2765 | 18.3325 | 14.9683 | 27.1962 | 21.8407 | 21.1475 | 35.7537 | 28.9893 | 40.2157 | 37.9015 | 42.098 | 56.9873
BLD14PST |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.5966 | 14.8874 | 23.676 | 12.2735 | 18.3291 | 14.9659 | 27.1933 | 21.8378 | 21.145 | 35.7504 | 28.9862 | 40.2127 | 37.8982 | 42.0951 | 56.9845
BLD14PST |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6047 | 14.8963 | 23.6865 | 12.2812 | 18.3396 | 14.9738 | 27.2035 | 21.8492 | 21.1537 | 35.7629 | 28.9988 | 40.2254 | 37.9126 | 42.108 | 56.9996
BLD14PST |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 39.023 | 29.583 | 47.1394 | 24.3739 | 36.4396 | 29.7617 | 54.1857 | 43.4504 | 42.1103 | 71.2637 | 57.7323 | 80.1876 | 75.5307 | 83.9496 | 113.6946
BLD14PST |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6051 | 14.8967 | 23.6869 | 12.2815 | 18.34 | 14.9741 | 27.2038 | 21.8495 | 21.154 | 35.7632 | 28.9991 | 40.2257 | 37.9129 | 42.1083 | 56.9999
BLD14PST |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.6029 | 14.8947 | 23.6822 | 12.279 | 18.3353 | 14.9703 | 27.1985 | 21.8431 | 21.1495 | 35.7563 | 28.9918 | 40.2181 | 37.904 | 42.1003 | 56.9894
BLD14PST |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 10.251 | 19.701 | 15.0085 | 23.7834 | 12.3658 | 18.4349 | 15.0391 | 27.2816 | 21.9288 | 21.2197 | 35.8529 | 29.0844 | 40.3067 | 38.0019 | 42.1851 | 57.0731
BLD14PST |  |  | HVAC Efficiency
BLD14PST | COP |  | Air Conditioning (COP) | 3.4105 | 3.4285 | 3.4284 | 3.4303 | 3.4973 | 3.495 | 3.6102 | 3.4572 | 3.5338 | 3.6112 | 3.4313 | 3.5588 | 3.4092 | 3.4313 | 3.4081 | 3.4311
BLD14PST |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.5
BLD14PST |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 3.23 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.3 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
BLD14PST |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PST |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PST |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PST |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PST |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 3.3 | 3.3 | 3.3 | 3.3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.3 | 3.3
BLD14PST |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PST |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PST |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5
BLD14PST | EffHeat |  | Heating Efficiency (%) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.79319 | 0.79635 | 0.79319 | 0.79319 | 0.79319 | 0.79113
BLD14PST |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
BLD14PST |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD14PST |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PST |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PST |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PST |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PST |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78
BLD14PST |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PST |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PST |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14PST |  |  | HVAC Control - Economizer
BLD14PST |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
BLD14PST |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD14PST |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PST |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PST |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PST |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PST |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD14PST |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PST |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PST |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14PST | Fan |  | Fan Max Flow Rate (m3/s ) | 14.93 | 12.49 | 12.67 | 12.55 | 12.52 | 11.63 | 9.6 | 11.22 | 11.24 | 9.93 | 13.26 | 12.85 | 14.92 | 15.88 | 15.9 | 21.06
BLD14PST |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 1.64 | 1.05 | 1.23 | 1.05 | 1.01 | 1.01 | 0.74 | 1.11 | 1.1 | 0.87 | 1.5 | 1.46 | 1.69 | 1.81 | 1.81 | 2.38
BLD14PST |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 3.77 | 2.78 | 2.97 | 2.76 | 2.75 | 2.7 | 2.14 | 2.41 | 2.51 | 2.16 | 2.5 | 2.43 | 2.83 | 3.02 | 3.03 | 4
BLD14PST |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 1.37 | 1.28 | 1.21 | 1.29 | 1.29 | 1.21 | 1.05 | 1.19 | 1.21 | 1.07 | 1.19 | 1.12 | 1.22 | 1.23 | 1.23 | 1.64
BLD14PST |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 1.1 | 1 | 0.99 | 1.02 | 1.02 | 0.92 | 0.79 | 0.89 | 0.9 | 0.81 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
BLD14PST |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 1.07 | 0.98 | 0.96 | 0.99 | 0.99 | 0.9 | 0.76 | 0.87 | 0.87 | 0.78 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
BLD14PST |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 1.07 | 0.97 | 0.96 | 0.98 | 0.99 | 0.89 | 0.76 | 0.86 | 0.86 | 0.78 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
BLD14PST |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 1.91 | 1.73 | 1.7 | 1.74 | 1.74 | 1.57 | 1.31 | 1.52 | 1.48 | 1.35 | 2.01 | 1.95 | 2.28 | 2.44 | 2.45 | 3.25
BLD14PST |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 1 | 0.9 | 0.88 | 0.91 | 0.91 | 0.81 | 0.69 | 0.79 | 0.77 | 0.71 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
BLD14PST |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 0.99 | 0.9 | 0.88 | 0.9 | 0.91 | 0.81 | 0.68 | 0.79 | 0.77 | 0.7 | 1.01 | 0.98 | 1.15 | 1.23 | 1.23 | 1.63
BLD14PST |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 1.01 | 0.9 | 0.89 | 0.91 | 0.91 | 0.81 | 0.68 | 0.79 | 0.77 | 0.7 | 1.01 | 0.99 | 1.15 | 1.23 | 1.23 | 1.64
BLD14PST |  | Utility Costs
BLD14PST |  |  | Electric Utility Rates
BLD14PST |  |  | Average Annual Rate ($/kWh) | 0.085981 | 0.11851 | 0.098066 | 0.10031 | 0.1292 | 0.098601 | 0.14743 | 0.075138 | 0.037315 | 0.074674 | 0.092801 | 0.037317 | 0.05981 | 0.074528 | 0.058619 | 0.094569
BLD14PST |  |  | Total Cost ($/m2) | 28.03 | 32.89 | 27.75 | 25.53 | 30.6 | 25.64 | 32.3 | 18.17 | 8.89 | 16.47 | 22.49 | 8.83 | 14.64 | 17.94 | 14.04 | 24.64
BLD14PST |  |  | Gas Utility Rates
BLD14PST |  |  | Average Annual Rate ($/MJ) | 0.011402 | 0.0080428 | 0.0081367 | 0.0095074 | 0.0086118 | 0.0076272 | 0.0085626 | 0.0096568 | 0.0068692 | 0.0084142 | 0.0083001 | 0.0069032 | 0.0078719 | 0.0080778 | 0.0078601 | 0.0041214
BLD14PST |  |  | Total Cost ($/m2) | 0.11 | 1.17 | 0.93 | 2.91 | 0.83 | 1.49 | 2.24 | 5.19 | 2.61 | 4.08 | 6.24 | 3.77 | 7.7 | 6.49 | 9.52 | 8.13
BLD14PST |  |  | Total Utility Costs
BLD14PST |  |  | Cost Intensity ($/m2) | 28.15 | 34.06 | 28.69 | 28.44 | 31.43 | 27.13 | 34.53 | 23.36 | 11.5 | 20.55 | 28.73 | 12.59 | 22.34 | 24.43 | 23.56 | 32.77
BLD14PST |  | Energy - End Uses
BLD14PST |  |  | Electricity (kWh)
BLD14PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Cooling | 184266.6667 | 112600 | 123238.8889 | 63738.8889 | 28077.7778 | 81047.2222 | 7322.2222 | 44291.6667 | 36855.5556 | 8022.2222 | 32791.6667 | 23272.2222 | 26791.6667 | 13386.1111 | 8827.7778 | 3738.8889
BLD14PST |  |  | Interior Lighting | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500 | 292500
BLD14PST |  |  | Exterior Lighting | 59002.7778 | 58980.5556 | 58969.4444 | 58961.1111 | 58916.6667 | 58902.7778 | 58933.3333 | 58897.2222 | 58922.2222 | 58802.7778 | 58908.3333 | 58875 | 58869.4444 | 58855.5556 | 58822.2222 | 58461.1111
BLD14PST |  |  | Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
BLD14PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Fans | 104269.4444 | 74538.8889 | 75419.4444 | 75336.1111 | 74141.6667 | 69622.2222 | 57683.3333 | 68222.2222 | 68258.3333 | 60238.8889 | 80966.6667 | 78391.6667 | 91861.1111 | 96991.6667 | 98916.6667 | 148550
BLD14PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total End Uses | 681519.4444 | 580097.2222 | 591605.5556 | 532016.6667 | 495111.1111 | 543550 | 457919.4444 | 505391.6667 | 498011.1111 | 461044.4444 | 506641.6667 | 494516.6667 | 511497.2222 | 503211.1111 | 500541.6667 | 544727.7778
BLD14PST |  |  | Gas (MJ)
BLD14PST |  |  | Heating | 20930 | 304360 | 239280 | 640080 | 202040 | 408880 | 546110 | 1123780 | 794360 | 1013040 | 1571380 | 1140500 | 2045500 | 1679390 | 2531880 | 4123460
BLD14PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total End Uses | 20930 | 304360 | 239280 | 640080 | 202040 | 408880 | 546110 | 1123780 | 794360 | 1013040 | 1571380 | 1140500 | 2045500 | 1679390 | 2531880 | 4123460
BLD14PST |  |  | Purchased Cooling (MJ)
BLD14PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Purchased Heating (MJ)
BLD14PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total Building (MJ) | 2474400 | 2392710 | 2369070 | 2555330 | 1984440 | 2365670 | 2194610 | 2943190 | 2587200 | 2672800 | 3395290 | 2920760 | 3886900 | 3490950 | 4333830 | 6084480
BLD14PST |  | Energy - End Use Intensities
BLD14PST |  |  | Electricity (MJ/m2)
BLD14PST |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Cooling (elec) | 317.3485 | 193.9225 | 212.245 | 109.7727 | 48.3562 | 139.5815 | 12.6105 | 76.2802 | 63.4735 | 13.8161 | 56.4746 | 40.08 | 46.1413 | 23.0539 | 15.2034 | 6.4392
BLD14PST |  |  | Interior Lighting (elec) | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506 | 503.7506
BLD14PST |  |  | Exterior Lighting (elec) | 101.616 | 101.5777 | 101.5586 | 101.5443 | 101.4677 | 101.4438 | 101.4964 | 101.4342 | 101.4773 | 101.2716 | 101.4534 | 101.396 | 101.3864 | 101.3625 | 101.3051 | 100.6831
BLD14PST |  |  | Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
BLD14PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Fans (elec) | 179.5754 | 128.3727 | 129.8892 | 129.7457 | 127.6886 | 119.9051 | 99.3436 | 117.494 | 117.5562 | 103.7449 | 139.4428 | 135.008 | 158.2054 | 167.0414 | 170.3567 | 255.8364
BLD14PST |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total End Uses | 1173.7294 | 999.0576 | 1018.8775 | 916.2521 | 852.6924 | 936.115 | 788.64 | 870.3978 | 857.6869 | 794.022 | 872.5506 | 851.6686 | 880.913 | 866.6424 | 862.045 | 938.1434
BLD14PST |  |  | Gas (MJ/m2)
BLD14PST |  |  | Heating (gas) | 10.0128 | 145.6045 | 114.4705 | 306.2115 | 96.6551 | 195.6064 | 261.2566 | 537.6115 | 380.0184 | 484.6339 | 751.7414 | 545.6102 | 978.5583 | 803.4129 | 1211.2404 | 1972.6453
BLD14PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total End Uses | 10.0128 | 145.6045 | 114.4705 | 306.2115 | 96.6551 | 195.6064 | 261.2566 | 537.6115 | 380.0184 | 484.6339 | 751.7414 | 545.6102 | 978.5583 | 803.4129 | 1211.2404 | 1972.6453
BLD14PST |  |  | Purchased Cooling (MJ/m2)
BLD14PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Purchased Heating (MJ/m2)
BLD14PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total Building (MJ/m2) | 1183.7422 | 1144.6621 | 1133.3528 | 1222.4588 | 949.3475 | 1131.7262 | 1049.8919 | 1408.0093 | 1237.7052 | 1278.6559 | 1624.292 | 1397.2789 | 1859.4761 | 1670.0553 | 2073.2854 | 2910.7888
BLD14PST |  | Peak Energy Demand
BLD14PST |  |  | Electricity Peak Demand (kW)
BLD14PST |  |  | Jan | 151.875 | 129.6433 | 121.1975 | 111.1091 | 123.7558 | 107.8488 | 104.8852 | 106.5513 | 106.5815 | 105.2225 | 108.7885 | 108.6378 | 110.6292 | 111.7051 | 111.7336 | 120.1262
BLD14PST |  |  | Feb | 161.2532 | 129.7635 | 121.0756 | 108.5374 | 119.2404 | 110.8051 | 110.3555 | 106.5513 | 109.3355 | 105.2953 | 108.7885 | 108.3765 | 110.6292 | 111.7051 | 111.7336 | 120.1262
BLD14PST |  |  | Mar | 161.6141 | 132.9997 | 139.9083 | 116.1252 | 118.8241 | 110.743 | 104.8361 | 111.2814 | 109.1137 | 105.2225 | 108.7885 | 108.3591 | 110.6292 | 100.5033 | 111.7336 | 120.1262
BLD14PST |  |  | Apr | 169.3764 | 152.0499 | 143.9271 | 133.3819 | 127.737 | 134.6792 | 108.3888 | 111.8665 | 119.6036 | 101.6254 | 105.2512 | 111.8467 | 108.6757 | 98.4163 | 98.8319 | 106.6272
BLD14PST |  |  | May | 182.0987 | 164.593 | 167.7781 | 144.35 | 121.0839 | 148.9759 | 110.3379 | 128.3161 | 127.5458 | 108.2104 | 131.5707 | 120.7716 | 156.6421 | 115.9307 | 112.1106 | 112.0684
BLD14PST |  |  | Jun | 189.5886 | 167.0954 | 195.8494 | 158.254 | 123.8345 | 177.9383 | 111.8133 | 159.4259 | 140.9244 | 113.4891 | 157.7059 | 133.3694 | 154.2701 | 142.5481 | 131.223 | 129.1781
BLD14PST |  |  | Jul | 182.0984 | 173.0166 | 192.2219 | 173.7236 | 130.7825 | 174.1913 | 121.5404 | 166.2414 | 146.3072 | 124.7929 | 161.1805 | 141.5792 | 161.3828 | 143.5059 | 145.9516 | 136.4676
BLD14PST |  |  | Aug | 191.781 | 172.8423 | 192.0455 | 162.5702 | 141.4515 | 167.739 | 116.6136 | 166.1445 | 142.926 | 120.0471 | 157.5578 | 142.9763 | 152.4149 | 137.9098 | 144.915 | 128.8724
BLD14PST |  |  | Sep | 182.1956 | 169.2129 | 177.8835 | 150.465 | 142.113 | 164.3095 | 135.2407 | 141.9637 | 128.9196 | 139.5998 | 136.2839 | 132.4375 | 132.7477 | 128.3562 | 121.5762 | 107.3007
BLD14PST |  |  | Oct | 178.5807 | 150.7902 | 146.1754 | 140.1981 | 132.4643 | 136.9624 | 109.6829 | 125.1131 | 116.1917 | 105.2225 | 124.0134 | 119.8442 | 119.1833 | 111.2794 | 117.3894 | 120.1262
BLD14PST |  |  | Nov | 164.0877 | 139.1921 | 135.8803 | 114.6112 | 125.7293 | 115.5319 | 105.3253 | 119.5133 | 109.1439 | 105.6915 | 121.8748 | 109.9764 | 110.869 | 111.7051 | 111.7336 | 120.1262
BLD14PST |  |  | Dec | 153.6085 | 136.1412 | 119.2566 | 109.7288 | 126.4283 | 112.442 | 104.8361 | 106.5513 | 106.5815 | 105.2225 | 108.7885 | 108.3591 | 110.6292 | 111.7051 | 111.7336 | 120.1262
BLD14PST |  |  | Time of Peak Electrical Demand
BLD14PST |  |  | Jan | 24-JAN-13:00 | 20-JAN-17:49 | 28-JAN-17:00 | 23-JAN-17:00 | 26-JAN-13:00 | 18-JAN-16:49 | 06-JAN-17:10 | 02-JAN-16:49 | 02-JAN-17:10 | 02-JAN-16:30 | 02-JAN-16:30 | 27-JAN-17:10 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
BLD14PST |  |  | Feb | 25-FEB-13:39 | 23-FEB-15:09 | 28-FEB-15:00 | 18-FEB-15:00 | 13-FEB-11:00 | 08-FEB-17:10 | 15-FEB-17:49 | 01-FEB-17:30 | 14-FEB-17:49 | 21-FEB-17:40 | 01-FEB-16:00 | 11-FEB-17:30 | 01-FEB-17:19 | 01-FEB-17:30 | 01-FEB-17:10 | 01-FEB-09:09
BLD14PST |  |  | Mar | 13-MAR-15:39 | 25-MAR-12:30 | 17-MAR-14:00 | 28-MAR-15:00 | 31-MAR-14:09 | 31-MAR-15:00 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-17:00 | 01-MAR-17:49 | 01-MAR-17:40 | 01-MAR-17:49 | 01-MAR-17:00 | 30-MAR-16:00 | 01-MAR-17:49 | 01-MAR-17:00
BLD14PST |  |  | Apr | 01-APR-15:09 | 29-APR-14:20 | 01-APR-15:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 06-APR-16:00 | 04-APR-14:00 | 01-APR-09:09
BLD14PST |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-15:00 | 15-MAY-14:00 | 30-MAY-12:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 30-MAY-16:00
BLD14PST |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-15:00 | 29-JUN-14:09 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-16:00
BLD14PST |  |  | Jul | 13-JUL-14:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-14:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-15:00
BLD14PST |  |  | Aug | 21-AUG-14:30 | 31-AUG-14:09 | 01-AUG-16:00 | 17-AUG-14:39 | 08-AUG-12:00 | 05-AUG-12:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-14:39
BLD14PST |  |  | Sep | 11-SEP-14:00 | 16-SEP-14:50 | 09-SEP-14:00 | 11-SEP-13:00 | 23-SEP-13:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 02-SEP-14:00 | 02-SEP-15:00 | 27-SEP-15:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 02-SEP-15:00
BLD14PST |  |  | Oct | 06-OCT-14:20 | 06-OCT-15:00 | 24-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-15:00 | 13-OCT-14:00 | 26-OCT-16:00 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 23-OCT-08:09
BLD14PST |  |  | Nov | 07-NOV-14:39 | 27-NOV-17:19 | 13-NOV-17:30 | 22-NOV-17:30 | 20-NOV-12:00 | 10-NOV-16:40 | 13-NOV-16:00 | 04-NOV-16:00 | 08-NOV-17:10 | 04-NOV-16:49 | 02-NOV-16:49 | 04-NOV-16:00 | 02-NOV-16:00 | 06-NOV-17:10 | 01-NOV-16:49 | 01-NOV-08:09
BLD14PST |  |  | Dec | 16-DEC-12:00 | 02-DEC-17:19 | 09-DEC-17:19 | 01-DEC-17:30 | 19-DEC-12:00 | 05-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
BLD14PST |  | Source Energy
BLD14PST |  |  | Total Source Energy (GJ) | 8161.02 | 7917.26 | 6997.8 | 7141.89 | 5737.17 | 7445.92 | 5698.48 | 7733.38 | 6816.09 | 3997.54 | 8183.54 | 7152.32 | 8562.56 | 8130.87 | 8958.13 | 11507.59
BLD14PST |  |  | Total Source Energy (MJ/m2) | 3904.2 | 3787.58 | 3347.72 | 3416.65 | 2744.64 | 3562.1 | 2726.13 | 3699.62 | 3260.79 | 1912.41 | 3914.97 | 3421.64 | 4096.3 | 3889.78 | 4285.53 | 5505.19
BLD14PST |  | Water Consumption (m3)
BLD14PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  | Emissions
BLD14PST |  |  | Carbon Equivalent (kg) | 187284.03 | 198986.428 | 182906.4895 | 175422.6782 | 61505.0376 | 190699.4509 | 63362.8629 | 156647.4652 | 217761.2384 | 51847.6277 | 298452.121 | 222575.0163 | 211968.26 | 214175.989 | 216988.961 | 227636.9247
BLD14PST |  |  | CO2 (kg) | 433882.727 | 501399.0654 | 432460.1189 | 405290.8404 | 165007.2914 | 455513.1098 | 171328.3874 | 364391.726 | 515413.5469 | 132547.506 | 705099.5097 | 530119.9969 | 510204.2958 | 515205.1648 | 526899.2978 | 598800.6535
BLD14PST |  |  | NOX (kg) | 764.2649 | 652.5967 | 721.1753 | 748.4969 | 141.7574 | 731.4137 | 148.1007 | 664.6582 | 869.2727 | 176.0834 | 1209.1641 | 879.8067 | 833.3099 | 838.6592 | 840.5396 | 676.0787
BLD14PST |  |  | SO2 (kg) | 2917.1833 | 2767.1486 | 2379.0337 | 1867.5471 | 1440.7714 | 2990.0747 | 1332.6361 | 1845.1816 | 2174.931 | 356.6213 | 3414.7838 | 2159.7562 | 1207.766 | 1344.0827 | 1182.0398 | 2773.9918
BLD14PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14PST |  |  | Hg (kg) | 0.0133 | 0.0078 | 0.0065 | 0.0069 | 0.0007 | 0.0056 | 0.0007 | 0.0076 | 0.0086 | 0.0015 | 0.0105 | 0.0085 | 0.009 | 0.0095 | 0.0089 | 0.0098
BLD14PST |  |  | Water for Electricity (m3) | 361.0406 | 943.8873 | 17573.3 | 3321.69 | 8693.06 | 14911.8 | 8040.03 | 114.7428 | 2261.37 | 4710.39 | 786.0249 | 2245.5 | 793.559 | 31875.5 | 776.5623 | 556.5384
BLD14NEW |  | Program
BLD14NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD14NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD14NEW |  |  | Weighting Factor | 80.8338 | 582.608 | 149.0862 | 600.2213 |  | 367.8693 | 60.7796 | 592.9458 | 13.2453 | 62.7627 | 601.4542 | 118.36 | 89.7707 | 9.3991 | 4.0338 | 0.78933
BLD14NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD14NEW |  |  | Exterior walls
BLD14NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD14NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
BLD14NEW |  |  | Roof
BLD14NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD14NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD14NEW |  |  | Window
BLD14NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD14NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD14NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD14NEW |  |  | Skylights/TDD
BLD14NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD14NEW |  |  | Foundation
BLD14NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD14NEW |  |  | Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
BLD14NEW |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD14NEW |  | HVAC
BLD14NEW |  |  | HVAC Sizing
BLD14NEW | HVAC |  | Air Conditioning (kW) | 194.5732 | 198.0517 | 190.8755 | 193.9599 | 148.3206 | 168.9427 | 108.6552 | 186.4162 | 135.2865 | 121.9008 | 174.3013 | 126.3008 | 172.4897 | 116.4107 | 156.1244 | 132.2385
BLD14NEW |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 16.8202 | 17.2856 | 17.4382 | 16.8634 | 12.5214 | 15.044 | 9.1094 | 16.1856 | 11.588 | 10.5738 | 14.982 | 11.6279 | 16.9283 | 13.0294 | 17.5887 | 15.1149
BLD14NEW |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 39.8697 | 40.6324 | 39.1821 | 39.8956 | 28.3209 | 32.8377 | 20.9003 | 38.1571 | 26.4111 | 23.2536 | 34.308 | 23.4252 | 33.4226 | 21.3168 | 27.8422 | 24.9498
BLD14NEW |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 18.2522 | 17.9943 | 17.3751 | 17.7142 | 13.515 | 15.1293 | 10.2329 | 17.0461 | 12.3785 | 11.318 | 16.2641 | 11.7449 | 15.9496 | 10.2713 | 13.4137 | 10.3593
BLD14NEW |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 16.1871 | 16.3806 | 15.7371 | 16.0673 | 12.5193 | 14.089 | 9.2928 | 15.4783 | 11.3619 | 10.3488 | 14.7104 | 10.7452 | 14.3912 | 9.3045 | 12.1853 | 10.2722
BLD14NEW |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 15.8673 | 16.2204 | 15.5675 | 15.9017 | 12.4139 | 13.9718 | 9.1859 | 15.3175 | 11.252 | 10.2404 | 14.5457 | 10.6333 | 14.2264 | 9.1972 | 12.182 | 10.2564
BLD14NEW |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 15.6248 | 16.1498 | 15.4822 | 15.8262 | 12.3607 | 13.9081 | 9.1214 | 15.2427 | 11.1904 | 10.1793 | 14.4648 | 10.5128 | 14.1448 | 9.135 | 12.1999 | 10.2583
BLD14NEW |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 28.113 | 28.6722 | 27.4127 | 27.9867 | 22.0177 | 25.027 | 15.8542 | 26.9318 | 20.0484 | 17.8857 | 25.4068 | 18.6414 | 24.7774 | 17.4963 | 24.0361 | 20.2285
BLD14NEW |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 14.6198 | 14.9077 | 14.2079 | 14.5696 | 11.5597 | 12.9652 | 8.3262 | 14.0213 | 10.3569 | 9.3672 | 13.2167 | 9.6672 | 12.8927 | 8.8595 | 12.2002 | 10.2458
BLD14NEW |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 14.5599 | 14.849 | 14.1592 | 14.5119 | 11.5231 | 12.9175 | 8.2959 | 13.965 | 10.3238 | 9.3351 | 13.1606 | 9.634 | 12.8371 | 8.8572 | 12.1879 | 10.2368
BLD14NEW |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 14.6592 | 14.9596 | 14.3136 | 14.6234 | 11.5687 | 13.053 | 8.3362 | 14.0706 | 10.3755 | 9.3989 | 13.2423 | 9.669 | 12.9194 | 8.9434 | 12.2884 | 10.3164
BLD14NEW | HEAT |  | Heating (kW) | 123.0115 | 163.3658 | 137.0094 | 180.2579 | 127.9373 | 150.1105 | 141.4129 | 209.0666 | 170.5872 | 171.1758 | 268.6911 | 223.1061 | 307.4366 | 291.6122 | 320.3789 | 420.4533
BLD14NEW |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 10.251 | 14.5065 | 11.4175 | 17.5031 | 10.6614 | 13.9776 | 11.7844 | 20.7905 | 17.1262 | 16.0026 | 26.0763 | 21.7872 | 29.8199 | 28.3774 | 30.69 | 40.3981
BLD14NEW |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 27.0653 | 22.8349 | 31.3703 | 21.3229 | 25.0498 | 23.5688 | 37.3763 | 30.588 | 28.691 | 47.549 | 39.553 | 54.3953 | 51.6453 | 56.3834 | 74.1328
BLD14NEW |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.8429 | 13.7278 | 14.0536 | 21.7513 | 18.0502 | 24.8886 | 23.5992 | 26.0036 | 34.0851
BLD14NEW |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7701 | 13.6582 | 14.0536 | 21.6816 | 17.9829 | 24.8112 | 23.52 | 25.935 | 34.0033
BLD14NEW |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7665 | 13.6548 | 14.0536 | 21.6784 | 17.9798 | 24.8078 | 23.5165 | 25.9321 | 33.9999
BLD14NEW |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7778 | 13.6667 | 14.0536 | 21.6917 | 17.9934 | 24.823 | 23.5328 | 25.9478 | 34.0179
BLD14NEW |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 20.5019 | 27.0653 | 22.8349 | 29.1965 | 21.3229 | 24.6851 | 23.5688 | 33.3102 | 27.0749 | 28.1072 | 43.1056 | 35.7028 | 49.3329 | 46.734 | 51.5758 | 67.6772
BLD14NEW |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7782 | 13.6671 | 14.0536 | 21.6921 | 17.9937 | 24.8234 | 23.5331 | 25.9481 | 34.0183
BLD14NEW |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.7731 | 13.661 | 14.0536 | 21.6842 | 17.9853 | 24.814 | 23.5228 | 25.9372 | 34.006
BLD14NEW |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 10.251 | 13.5327 | 11.4175 | 14.5983 | 10.6614 | 12.3426 | 11.7844 | 16.881 | 13.7625 | 14.0536 | 21.7808 | 18.0778 | 24.9205 | 23.6311 | 26.0257 | 34.1148
BLD14NEW |  |  | HVAC Efficiency
BLD14NEW | COP |  | Air Conditioning (COP) | 3.5696 | 3.5695 | 3.6107 | 3.5694 | 3.6123 | 3.6118 | 3.6373 | 3.6106 | 3.6116 | 3.6376 | 3.6118 | 3.6385 | 3.6126 | 3.6389 | 3.6135 | 3.6119
BLD14NEW |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD14NEW |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_COOLCOIL | 3.3 | 3.3 | 3.5 | 3.3 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD14NEW |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD14NEW |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD14NEW |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD14NEW |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD14NEW |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.5 | 3.67 | 3.5 | 3.5
BLD14NEW |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD14NEW |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD14NEW |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD14NEW | EffHeat |  | Heating Efficiency (%) | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.79325
BLD14NEW |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14NEW |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
BLD14NEW |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14NEW |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14NEW |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14NEW |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14NEW |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
BLD14NEW |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14NEW |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14NEW |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD14NEW |  |  | HVAC Control - Economizer
BLD14NEW |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD14NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 7.85 | 7.97 | 7.71 | 7.82 | 6.68 | 7.15 | 5.88 | 7.5 | 7.36 | 6.18 | 7 | 6.75 | 6.95 | 6.8 | 6.36 | 7.97
BLD14NEW |  |  | PSZ-AC_10:10_UNITARY_PACKAGE_FAN | 0.68 | 0.7 | 0.7 | 0.68 | 0.56 | 0.64 | 0.49 | 0.65 | 0.62 | 0.54 | 0.6 | 0.6 | 0.68 | 0.75 | 0.71 | 0.9
BLD14NEW |  |  | PSZ-AC_1:1_UNITARY_PACKAGE_FAN | 1.61 | 1.64 | 1.61 | 1.61 | 1.38 | 1.53 | 1.19 | 1.54 | 1.57 | 1.28 | 1.38 | 1.36 | 1.35 | 1.29 | 1.19 | 1.51
BLD14NEW |  |  | PSZ-AC_2:2_UNITARY_PACKAGE_FAN | 0.74 | 0.72 | 0.7 | 0.71 | 0.62 | 0.65 | 0.56 | 0.69 | 0.69 | 0.58 | 0.65 | 0.64 | 0.64 | 0.61 | 0.55 | 0.62
BLD14NEW |  |  | PSZ-AC_3:3_UNITARY_PACKAGE_FAN | 0.65 | 0.66 | 0.63 | 0.65 | 0.56 | 0.59 | 0.5 | 0.62 | 0.61 | 0.52 | 0.59 | 0.57 | 0.58 | 0.55 | 0.49 | 0.62
BLD14NEW |  |  | PSZ-AC_4:4_UNITARY_PACKAGE_FAN | 0.64 | 0.65 | 0.63 | 0.64 | 0.55 | 0.58 | 0.49 | 0.62 | 0.61 | 0.51 | 0.59 | 0.56 | 0.57 | 0.54 | 0.49 | 0.62
BLD14NEW |  |  | PSZ-AC_5:5_UNITARY_PACKAGE_FAN | 0.63 | 0.65 | 0.62 | 0.64 | 0.55 | 0.58 | 0.49 | 0.61 | 0.6 | 0.51 | 0.58 | 0.56 | 0.57 | 0.53 | 0.49 | 0.62
BLD14NEW |  |  | PSZ-AC_6:6_UNITARY_PACKAGE_FAN | 1.13 | 1.15 | 1.1 | 1.13 | 0.96 | 1.01 | 0.84 | 1.08 | 1.04 | 0.87 | 1.02 | 0.96 | 1 | 1 | 0.97 | 1.22
BLD14NEW |  |  | PSZ-AC_7:7_UNITARY_PACKAGE_FAN | 0.59 | 0.6 | 0.57 | 0.59 | 0.5 | 0.52 | 0.44 | 0.56 | 0.54 | 0.46 | 0.53 | 0.5 | 0.52 | 0.51 | 0.49 | 0.62
BLD14NEW |  |  | PSZ-AC_8:8_UNITARY_PACKAGE_FAN | 0.59 | 0.6 | 0.57 | 0.58 | 0.5 | 0.52 | 0.44 | 0.56 | 0.54 | 0.45 | 0.53 | 0.5 | 0.52 | 0.51 | 0.49 | 0.62
BLD14NEW |  |  | PSZ-AC_9:9_UNITARY_PACKAGE_FAN | 0.59 | 0.6 | 0.58 | 0.59 | 0.5 | 0.53 | 0.44 | 0.57 | 0.54 | 0.46 | 0.53 | 0.5 | 0.52 | 0.51 | 0.49 | 0.62
BLD14NEW |  | Utility Costs
BLD14NEW |  |  | Electric Utility Rates
BLD14NEW |  |  | Average Annual Rate ($/kWh) | 0.08417 | 0.11895 | 0.10378 | 0.10309 | 0.12898 | 0.098564 | 0.14785 | 0.074736 | 0.037586 | 0.074496 | 0.052552 | 0.037618 | 0.059897 | 0.073823 | 0.058412 | 0.09466
BLD14NEW |  |  | Total Cost ($/m2) | 14.93 | 19.55 | 17.2 | 15.28 | 17.13 | 15.02 | 18.61 | 10.67 | 5.26 | 9.48 | 7.21 | 5.02 | 8.13 | 9.66 | 7.5 | 12.45
BLD14NEW |  |  | Gas Utility Rates
BLD14NEW |  |  | Average Annual Rate ($/MJ) | 0.011423 | 0.0080373 | 0.0081355 | 0.0095161 | 0.0086334 | 0.0076343 | 0.0085558 | 0.0096545 | 0.0068797 | 0.0084119 | 0.0083152 | 0.0069175 | 0.007859 | 0.0081232 | 0.007858 | 0.0041323
BLD14NEW |  |  | Total Cost ($/m2) | 0.05 | 0.79 | 0.71 | 2 | 0.59 | 1.11 | 1.68 | 3.58 | 1.83 | 3.16 | 4.25 | 2.67 | 5.31 | 4.79 | 6.65 | 5.71
BLD14NEW |  |  | Total Utility Costs
BLD14NEW |  |  | Cost Intensity ($/m2) | 14.99 | 20.34 | 17.92 | 17.27 | 17.72 | 16.13 | 20.29 | 14.25 | 7.09 | 12.64 | 11.46 | 7.69 | 13.44 | 14.45 | 14.15 | 18.16
BLD14NEW |  | Energy - End Uses
BLD14NEW |  |  | Electricity (kWh)
BLD14NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Cooling | 99236.1111 | 71150 | 75583.3333 | 38308.3333 | 12719.4444 | 51188.8889 | 2958.3333 | 28688.8889 | 23680.5556 | 4255.5556 | 19513.8889 | 13413.8889 | 16433.3333 | 7605.5556 | 4669.4444 | 961.1111
BLD14NEW |  |  | Interior Lighting | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725 | 132725
BLD14NEW |  |  | Exterior Lighting | 50200 | 50180.5556 | 50172.2222 | 50163.8889 | 50125 | 50113.8889 | 50141.6667 | 50111.1111 | 50130.5556 | 50030.5556 | 50119.4444 | 50088.8889 | 50086.1111 | 50075 | 50047.2222 | 49738.8889
BLD14NEW |  |  | Interior Equipment | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778 | 41477.7778
BLD14NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Fans | 47202.7778 | 48055.5556 | 46561.1111 | 47125 | 40513.8889 | 43063.8889 | 35822.2222 | 45433.3333 | 44541.6667 | 37583.3333 | 42958.3333 | 41252.7778 | 42861.1111 | 41733.3333 | 39558.3333 | 50094.4444
BLD14NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total End Uses | 370844.4444 | 343588.8889 | 346516.6667 | 309800 | 277563.8889 | 318569.4444 | 263125 | 298436.1111 | 292555.5556 | 266072.2222 | 286794.4444 | 278958.3333 | 283583.3333 | 273616.6667 | 268477.7778 | 274997.2222
BLD14NEW |  |  | Gas (MJ)
BLD14NEW |  |  | Heating | 9840 | 205170 | 182960 | 438270 | 143750 | 303730 | 409700 | 775540 | 555250 | 785120 | 1068970 | 807880 | 1413150 | 1231530 | 1768930 | 2885950
BLD14NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total End Uses | 9840 | 205170 | 182960 | 438270 | 143750 | 303730 | 409700 | 775540 | 555250 | 785120 | 1068970 | 807880 | 1413150 | 1231530 | 1768930 | 2885950
BLD14NEW |  |  | Purchased Cooling (MJ)
BLD14NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Purchased Heating (MJ)
BLD14NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total Building (MJ) | 1344880 | 1442090 | 1430420 | 1553550 | 1142980 | 1450580 | 1356950 | 1849910 | 1608450 | 1742980 | 2101420 | 1812130 | 2434050 | 2216550 | 2735450 | 3875940
BLD14NEW |  | Energy - End Use Intensities
BLD14NEW |  |  | Electricity (MJ/m2)
BLD14NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Cooling (elec) | 170.9068 | 122.5363 | 130.1715 | 65.9755 | 21.9057 | 88.1588 | 5.0949 | 49.4087 | 40.7832 | 7.329 | 33.6073 | 23.1017 | 28.3019 | 13.0985 | 8.0418 | 1.6552
BLD14NEW |  |  | Interior Lighting (elec) | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822 | 228.5822
BLD14NEW |  |  | Exterior Lighting (elec) | 86.4557 | 86.4222 | 86.4078 | 86.3935 | 86.3265 | 86.3074 | 86.3552 | 86.3026 | 86.3361 | 86.1638 | 86.3169 | 86.2643 | 86.2595 | 86.2404 | 86.1925 | 85.6615
BLD14NEW |  |  | Interior Equipment (elec) | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434 | 71.434
BLD14NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Fans (elec) | 81.2938 | 82.7624 | 80.1887 | 81.1598 | 69.774 | 74.1657 | 61.6939 | 78.2464 | 76.7107 | 64.7269 | 73.9839 | 71.0465 | 73.8164 | 71.8742 | 68.1283 | 86.2739
BLD14NEW |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total End Uses | 638.6773 | 591.7372 | 596.7794 | 533.5451 | 478.0273 | 548.6481 | 453.1603 | 513.9739 | 503.8463 | 458.2361 | 493.9244 | 480.4288 | 488.3941 | 471.2293 | 462.379 | 473.6069
BLD14NEW |  |  | Gas (MJ/m2)
BLD14NEW |  |  | Heating (gas) | 4.7074 | 98.1524 | 87.5273 | 209.6665 | 68.7694 | 145.3031 | 195.9987 | 371.015 | 265.6292 | 375.598 | 511.3906 | 386.4863 | 676.0448 | 589.1586 | 846.2484 | 1380.6259
BLD14NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total End Uses | 4.7074 | 98.1524 | 87.5273 | 209.6665 | 68.7694 | 145.3031 | 195.9987 | 371.015 | 265.6292 | 375.598 | 511.3906 | 386.4863 | 676.0448 | 589.1586 | 846.2484 | 1380.6259
BLD14NEW |  |  | Purchased Cooling (MJ/m2)
BLD14NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Purchased Heating (MJ/m2)
BLD14NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total Building (MJ/m2) | 643.3847 | 689.8896 | 684.3067 | 743.2116 | 546.7967 | 693.9512 | 649.159 | 884.9889 | 769.4755 | 833.8341 | 1005.3102 | 866.9151 | 1164.4389 | 1060.3879 | 1308.6274 | 1854.2328
BLD14NEW |  | Peak Energy Demand
BLD14NEW |  |  | Electricity Peak Demand (kW)
BLD14NEW |  |  | Jan | 80.5322 | 72.5038 | 67.7965 | 61.6221 | 65.6437 | 60.5691 | 59.1994 | 60.9955 | 60.835 | 59.532 | 60.5041 | 60.1896 | 60.4207 | 60.2298 | 59.7436 | 61.5105
BLD14NEW |  |  | Feb | 82.3318 | 71.5697 | 65.2203 | 56.2512 | 61.8542 | 61.2367 | 60.275 | 60.9955 | 61.2301 | 59.532 | 60.5041 | 60.1896 | 60.4207 | 60.2298 | 59.7436 | 61.5105
BLD14NEW |  |  | Mar | 83.5564 | 73.7607 | 78.0258 | 60.9842 | 61.028 | 60.5691 | 59.1994 | 60.9955 | 61.1512 | 59.532 | 60.5041 | 60.1896 | 60.4207 | 50.8097 | 59.7436 | 61.5105
BLD14NEW |  |  | Apr | 88.1118 | 88.1904 | 82.0179 | 73.2331 | 64.8378 | 76.2491 | 56.8709 | 60.3513 | 65.8177 | 53.042 | 54.2965 | 58.5835 | 52.8959 | 48.964 | 48.2586 | 50.0255
BLD14NEW |  |  | May | 96.1337 | 96.5263 | 98.5019 | 81.7552 | 59.8026 | 86.9754 | 57.8614 | 72.3364 | 72.1997 | 57.459 | 70.1574 | 64.7243 | 86.6027 | 58.1757 | 55.6104 | 50.5964
BLD14NEW |  |  | Jun | 100.2006 | 98.1012 | 115.1251 | 91.1533 | 62.5568 | 105.2614 | 58.6087 | 95.8784 | 82.7911 | 61.7471 | 89.1331 | 73.9923 | 87.0757 | 75.9358 | 67.833 | 59.8624
BLD14NEW |  |  | Jul | 96.7278 | 102.246 | 112.4395 | 101.5168 | 68.8588 | 103.4565 | 65.5135 | 100.272 | 86.5746 | 70.038 | 92.3645 | 80.2994 | 92.1617 | 77.168 | 78.089 | 63.9649
BLD14NEW |  |  | Aug | 101.0055 | 102.2638 | 113.5053 | 94.282 | 74.7248 | 99.5675 | 62.255 | 100.3903 | 84.3008 | 66.6026 | 90.6506 | 81.0879 | 86.6161 | 72.4585 | 78.1739 | 59.5231
BLD14NEW |  |  | Sep | 95.6332 | 100.701 | 103.9566 | 86.3184 | 74.3807 | 97.079 | 76.4502 | 83.8793 | 73.8406 | 80.26 | 75.1071 | 73.208 | 71.6517 | 66.4066 | 62.0277 | 50.0255
BLD14NEW |  |  | Oct | 93.6303 | 87.2302 | 82.9775 | 77.5676 | 67.2753 | 77.6298 | 58.5235 | 70.6522 | 63.9288 | 59.532 | 66.814 | 64.2477 | 62.4479 | 55.0939 | 59.7436 | 61.5105
BLD14NEW |  |  | Nov | 87.1243 | 79.5876 | 78.0715 | 62.5134 | 64.887 | 64.4048 | 59.1994 | 66.3163 | 61.3494 | 59.532 | 65.0918 | 60.1896 | 60.4207 | 60.2298 | 59.7436 | 61.5105
BLD14NEW |  |  | Dec | 83.0418 | 76.9582 | 66.5781 | 61.3354 | 63.1223 | 61.7655 | 59.1994 | 60.9955 | 60.835 | 59.532 | 60.5041 | 60.1896 | 60.4207 | 60.2298 | 59.7436 | 61.5105
BLD14NEW |  |  | Time of Peak Electrical Demand
BLD14NEW |  |  | Jan | 23-JAN-17:00 | 20-JAN-17:49 | 28-JAN-17:00 | 23-JAN-17:00 | 25-JAN-17:19 | 02-JAN-16:40 | 02-JAN-16:00 | 02-JAN-16:49 | 02-JAN-17:10 | 02-JAN-16:30 | 02-JAN-16:30 | 02-JAN-16:49 | 02-JAN-16:40 | 02-JAN-16:49 | 02-JAN-16:30 | 02-JAN-09:09
BLD14NEW |  |  | Feb | 25-FEB-13:00 | 23-FEB-15:30 | 28-FEB-15:00 | 18-FEB-15:00 | 11-FEB-17:30 | 08-FEB-17:10 | 15-FEB-17:49 | 01-FEB-17:30 | 14-FEB-17:49 | 01-FEB-17:10 | 01-FEB-16:00 | 01-FEB-17:19 | 01-FEB-17:19 | 01-FEB-17:30 | 01-FEB-17:10 | 01-FEB-09:09
BLD14NEW |  |  | Mar | 13-MAR-14:00 | 25-MAR-12:30 | 17-MAR-14:00 | 28-MAR-15:00 | 04-MAR-17:49 | 01-MAR-17:40 | 01-MAR-17:00 | 01-MAR-17:00 | 02-MAR-17:00 | 01-MAR-17:49 | 01-MAR-17:40 | 01-MAR-17:49 | 01-MAR-17:00 | 30-MAR-15:00 | 01-MAR-17:49 | 01-MAR-17:00
BLD14NEW |  |  | Apr | 01-APR-15:39 | 29-APR-14:30 | 01-APR-15:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-14:09 | 29-APR-15:09 | 07-APR-14:00 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 01-APR-09:09 | 01-APR-09:09
BLD14NEW |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-15:00 | 15-MAY-14:00 | 30-MAY-14:09 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
BLD14NEW |  |  | Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-14:00 | 29-JUN-14:00 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-14:00 | 20-JUN-16:00
BLD14NEW |  |  | Jul | 13-JUL-14:00 | 29-JUL-14:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-16:00
BLD14NEW |  |  | Aug | 21-AUG-14:00 | 31-AUG-14:09 | 01-AUG-16:00 | 17-AUG-14:50 | 08-AUG-14:00 | 04-AUG-15:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
BLD14NEW |  |  | Sep | 07-SEP-13:00 | 16-SEP-14:50 | 09-SEP-15:30 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:30 | 02-SEP-15:20 | 02-SEP-15:00 | 05-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 01-SEP-08:09
BLD14NEW |  |  | Oct | 06-OCT-14:30 | 06-OCT-15:00 | 24-OCT-14:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-14:00 | 13-OCT-14:00 | 26-OCT-16:00 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 26-OCT-16:00 | 23-OCT-08:09
BLD14NEW |  |  | Nov | 07-NOV-17:40 | 27-NOV-17:19 | 13-NOV-17:30 | 22-NOV-17:30 | 20-NOV-16:49 | 10-NOV-16:40 | 06-NOV-17:10 | 04-NOV-16:00 | 08-NOV-17:10 | 01-NOV-16:49 | 02-NOV-16:49 | 01-NOV-16:00 | 01-NOV-16:00 | 06-NOV-17:10 | 18-NOV-16:30 | 01-NOV-08:09
BLD14NEW |  |  | Dec | 15-DEC-17:30 | 02-DEC-17:19 | 09-DEC-17:19 | 01-DEC-17:30 | 18-DEC-16:49 | 05-DEC-16:30 | 01-DEC-16:49 | 01-DEC-16:40 | 01-DEC-16:00 | 01-DEC-16:19 | 01-DEC-16:19 | 01-DEC-16:40 | 01-DEC-16:30 | 01-DEC-16:40 | 01-DEC-16:19 | 01-DEC-09:09
BLD14NEW |  | Source Energy
BLD14NEW |  |  | Total Source Energy (GJ) | 4439.06 | 4716.53 | 4145.52 | 4230.39 | 3249.59 | 4433.96 | 3379.13 | 4688.84 | 4100.85 | 2525.94 | 4828.4 | 4214.31 | 5052 | 4768.77 | 5253.59 | 6687.7
BLD14NEW |  |  | Total Source Energy (MJ/m2) | 2123.63 | 2256.37 | 1983.2 | 2023.8 | 1554.59 | 2121.19 | 1616.56 | 2243.12 | 1961.83 | 1208.4 | 2309.89 | 2016.11 | 2416.86 | 2281.36 | 2513.3 | 3199.37
BLD14NEW |  | Water Consumption (m3)
BLD14NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  | Emissions
BLD14NEW |  |  | Carbon Equivalent (kg) | 101881.1397 | 118307.2791 | 107904.4325 | 103332.9548 | 35029.8961 | 112922.6221 | 38138.2962 | 94519.681 | 129521.16 | 33536.9159 | 172180.0466 | 128522.4109 | 122551.7758 | 122197.7213 | 123796.519 | 129422.1427
BLD14NEW |  |  | CO2 (kg) | 236013.0338 | 298272.4319 | 255531.9852 | 239421.2537 | 94092.558 | 270310.3846 | 103443.4865 | 221007.1517 | 307394.9297 | 86939.3586 | 408483.4391 | 307614.7478 | 297406.9956 | 296726.2252 | 304022.0762 | 344197.7855
BLD14NEW |  |  | NOX (kg) | 415.7952 | 387.7062 | 424.4336 | 438.9601 | 80.9122 | 431.7053 | 89.6363 | 397.7788 | 514.8433 | 111.1019 | 692.9563 | 504.0852 | 475.2031 | 471.0736 | 470.2778 | 379.3497
BLD14NEW |  |  | SO2 (kg) | 1587.361 | 1638.9696 | 1393.4664 | 1087.5152 | 807.7141 | 1752.4698 | 765.7692 | 1089.6194 | 1277.6817 | 205.8623 | 1933.0442 | 1218.3744 | 669.6827 | 730.9197 | 634.1238 | 1400.6177
BLD14NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD14NEW |  |  | Hg (kg) | 0.0072 | 0.0046 | 0.0038 | 0.004 | 0.0004 | 0.0033 | 0.0004 | 0.0045 | 0.005 | 0.0009 | 0.0059 | 0.0048 | 0.005 | 0.0052 | 0.0048 | 0.0051
BLD14NEW |  |  | Water for Electricity (m3) | 196.4573 | 559.0579 | 10293.1 | 1934.27 | 4873.39 | 8739.64 | 4619.87 | 67.7562 | 1328.44 | 2718.4 | 444.9427 | 1266.7 | 439.9638 | 17332 | 416.5267 | 280.9588

## Picture
DOE Commercial Building Benchmark - Strip Mall

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
| Sat |  |  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
| Sat |  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 43.5 | 2268.21
[5 empty] | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
|  | INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
[5 empty] | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
[5 empty] | WinterDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
| Sat |  |  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
[5 empty] | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
| Sun |  |  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 2737.8 | 142756.71
[5 empty] | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
[5 empty] | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
| Sat |  |  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
| Sun |  |  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  | HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 91 | 4745
[5 empty] | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
|  | MinOA_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 91 | 4745
[5 empty] | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
SchGas | WD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sat |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0