## 1
1 | Building Summary Full Service Restaurant
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 511.15 | 511.15 | 511.15
nFloor |  | Number of Floors | 1 | 1 | 1
glazing |  | Total | 0.182 | 0.182 | 0.182
hCeiling |  | Floor to Ceiling Height (m) | 3.048 | 3.048 | 3.048
areaWall |  | Gross Dimensions - Total Area (m2) | 275.72 | 275.72 | 275.72
ver2hor |  | Wall to Skin Ratio | 0.35 | 0.326 | 0.326
areaRoof |  | Gross Dimensions - Total Area (m2) | 569.52 | 569.52 | 569.52
areaWindow |  | Total Area (m2) | 50.18 | 50.18 | 50.18

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD1PRE | Total | Total Conditioned Zones |  |  | 511.16 | 1558.41 | 0 | 275.7203 | 47.17 | 0 | 196.056 | 24.389 | 146.5864 | 326.8278 | 503.4582 | 9.4545 | 5.3362 | 1956.4676 | 0 | 2.0608
BLD1PST | Total | Total Conditioned Zones |  |  | 511.16 | 1558.41 | 0 | 275.7203 | 47.17 | 0 | 196.056 | 24.389 | 146.5864 | 326.8278 | 503.4582 | 9.4545 | 5.3362 | 1956.4676 | 0 | 2.0608
BLD1NEW | Total | Total Conditioned Zones |  |  | 511.16 | 1558.41 | 0 | 275.7203 | 47.17 | 0 | 196.056 | 19.9621 | 146.5864 | 326.8278 | 503.4582 | 9.4545 | 5.3362 | 1956.4676 | 0 | 0.54954

## 3
3 | UWG | Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD1PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD1PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD1PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD1PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD1PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD1PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD1PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD1PRE | HVAC |  | Air Conditioning (kW) | 126.2887 | 130.1745 | 135.6321 | 131.72 | 114.9804 | 135.3304 | 81.2161 | 122.3538 | 113.7252 | 94.6671 | 114.4349 | 103.7584 | 113.9645 | 84.5784 | 108.9161 | 93.2676
BLD1PRE | HEAT |  | Heating (kW) | 174.4971 | 224.2671 | 199.5291 | 239.6737 | 167.7056 | 210.7678 | 169.6649 | 251.1949 | 214.0258 | 206.3555 | 282.7693 | 235.9525 | 310.1068 | 288.8506 | 316.885 | 446.7323
BLD1PRE | COP |  | Air Conditioning (COP) | 3.2824 | 3.2825 | 3.2832 | 3.2823 | 3.2788 | 3.2829 | 3.3628 | 3.2805 | 3.2878 | 3.3097 | 3.2865 | 3.2883 | 3.2941 | 3.3455 | 3.3022 | 3.355
BLD1PRE | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD1PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 6.98 | 7.13 | 7.36 | 7.2 | 6.55 | 7.34 | 6.11 | 6.82 | 7.31 | 6.36 | 6.5 | 6.77 | 6.48 | 6.62 | 6.27 | 7.53
BLD1PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD1PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD1PST | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD1PST | RvalRoof |  | R-value attic floor (m2·K / W) | 2.38 | 2.6685 | 3.8287 | 2.4461 | 1.7612 | 3.6691 | 2.0013 | 3.0365 | 2.9851 | 2.7518 | 3.323 | 3.4533 | 3.9137 | 3.5943 | 4.403 | 5.6812
BLD1PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD1PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD1PST | HVAC |  | Air Conditioning (kW) | 119.7388 | 106.524 | 106.5113 | 107.401 | 107.4206 | 104.2248 | 68.7288 | 98.12 | 90.7687 | 77.3865 | 97.4747 | 85.1657 | 94.6949 | 69.3804 | 89.3295 | 56.6415
BLD1PST | HEAT |  | Heating (kW) | 169.5488 | 198.5556 | 169.935 | 213.7145 | 159.237 | 178.7099 | 154.6386 | 224.1564 | 194.4252 | 187.5927 | 258.795 | 222.6125 | 274.942 | 258.157 | 272.3827 | 332.4583
BLD1PST | COP |  | Air Conditioning (COP) | 3.2892 | 3.2855 | 3.2867 | 3.2862 | 3.2793 | 3.285 | 3.3603 | 3.2847 | 3.3163 | 3.3625 | 3.2844 | 3.3688 | 3.3185 | 3.3733 | 3.3154 | 3.3756
BLD1PST | EffHeat |  | Heating Efficiency (%) | 0.78483 | 0.78454 | 0.78457 | 0.78464 | 0.784 | 0.78446 | 0.78364 | 0.78438 | 0.78479 | 0.78401 | 0.78438 | 0.78475 | 0.78432 | 0.78454 | 0.78406 | 0.78
BLD1PST | Fan |  | Fan Max Flow Rate (m3/s ) | 6.71 | 6.18 | 6.18 | 6.21 | 6.22 | 6.08 | 5.52 | 5.84 | 6.44 | 5.63 | 5.81 | 6.22 | 5.71 | 5.93 | 5.49 | 5.31
BLD1NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD1NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
BLD1NEW | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD1NEW | RvalRoof |  | R-value attic floor (m2·K / W) | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 6.5229 | 6.5229 | 6.5229 | 6.5229
BLD1NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD1NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD1NEW | HVAC |  | Air Conditioning (kW) | 93.1753 | 93.7839 | 93.1844 | 93.258 | 76.1909 | 91.4801 | 63.4188 | 90.641 | 83.8035 | 69.0879 | 89.6696 | 81.3529 | 89.139 | 67.7901 | 79.9157 | 53.8576
BLD1NEW | HEAT |  | Heating (kW) | 140.4075 | 183.6129 | 155.0762 | 197.5188 | 135.874 | 165.5506 | 147.113 | 214.9739 | 185.0393 | 177.7201 | 248.7759 | 216.0424 | 266.9188 | 252.145 | 267.6036 | 319.5478
BLD1NEW | COP |  | Air Conditioning (COP) | 3.3201 | 3.3195 | 3.3188 | 3.2869 | 3.3834 | 3.3215 | 3.3554 | 3.3193 | 3.3721 | 3.3643 | 3.319 | 3.3677 | 3.3172 | 3.3719 | 3.3516 | 3.3659
BLD1NEW | EffHeat |  | Heating Efficiency (%) | 0.78424 | 0.78428 | 0.78421 | 0.78442 | 0.7841 | 0.78431 | 0.78347 | 0.78423 | 0.78471 | 0.78388 | 0.78421 | 0.78468 | 0.78413 | 0.78446 | 0.78399 | 0.78356
BLD1NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 5.64 | 5.67 | 5.64 | 5.64 | 5.27 | 5.58 | 5.24 | 5.54 | 6.04 | 5.27 | 5.5 | 5.95 | 5.48 | 5.72 | 5.33 | 5.14

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Sat |  |  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Sun |  |  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| Sat |  |  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| Sun |  |  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
| Sat |  |  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
| Sun |  |  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | Other | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Sat |  |  |  |  | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Sun |  |  |  |  | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | SummerDesign | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| Sat |  |  |  |  | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| Sun |  |  |  |  | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
SchGas | WD | GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
| Sat |  |  |  | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
| Sun |  |  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
SchWater | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
| Sat |  |  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
| Sun |  |  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2

## BuildingSummary
UWG | Building Summary Full Service Restaurant
|  |  | Pre-80 | Post-80 | New
Program
|  | Building Name | Full Service Restaurant | Full Service Restaurant | Full Service Restaurant
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Food Service | Food Service | Food Service
Form
areaFloor |  | Total Floor Area (m2) | 511.15 | 511.15 | 511.15
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 1 | 1 | 1
nFloor |  | Number of Floors | 1 | 1 | 1
Window Fraction (Window to Wall Ratio)
|  | South | 0.28 | 0.28 | 0.28
|  | East | 0.224 | 0.224 | 0.224
|  | North | 0 | 0 | 0
|  | West | 0.224 | 0.224 | 0.224
glazing |  | Total | 0.182 | 0.182 | 0.182
|  | Skylight/TDD Percentage | 0 | 0 | 0
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | 2 zones | 2 zones plus attic | 2 zones plus attic
hCeiling |  | Floor to Ceiling Height (m) | 3.048 | 3.048 | 3.048
|  | Roof type | Built-up flat roof, insulation entirely above deck | Attic | Attic
Fabric
Exterior walls
|  | Construction Type | Steel frame wall | Steel frame wall | Steel frame wall
areaWall |  | Gross Dimensions - Total Area (m2) | 275.72 | 275.72 | 275.72
|  | Net Dimensions - Total Area (m2) | 225.54 | 225.54 | 225.54
ver2hor |  | Wall to Skin Ratio | 0.35 | 0.326 | 0.326
Roof
|  | Construction Type | IEAD | Attic | Attic
areaRoof |  | Gross Dimensions - Total Area (m2) | 569.52 | 569.52 | 569.52
|  | Net Dimensions - Total Area (m2) | 569.52 | 569.52 | 569.52
|  | Roof to Skin Ratio | 0.65 | 0.674 | 0.674
Window Dimensions (m2)
|  | South | 19.3 | 19.3 | 19.3
|  | East | 15.44 | 15.44 | 15.44
|  | North | 0 | 0 | 0
|  | West | 15.44 | 15.44 | 15.44
areaWindow |  | Total Area (m2) | 50.18 | 50.18 | 50.18
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) | 0 | 0 | 0
|  | Operable area (m2) | 0 | 0 | 0
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
|  | Dimensions - Total Area (m2) | 511.15 | 511.15 | 511.15
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 68.93 | 68.93 | 68.93
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 1022.31 | 1022.31 | 1022.31
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 2.0608 | 2.0608 | 0.55
HVAC
|  | System Type | PSZ-AC | PSZ-AC | PSZ-AC
|  | Heating Type | Gas furnace | Gas furnace | Gas furnace
|  | Cooling Type | Unitary DX | Unitary DX | Unitary DX
|  | Fan Control | Constant volume | Constant volume | Constant volume
Service Water Heating
|  | SWH Type | Storage Tank | Storage Tank | Storage Tank
|  | Fuel | Natural Gas | Natural Gas | Natural Gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3) | 1377.36 | 1377.36 | 1377.36

## ZoneSummary
Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD1PRE |  | Dining | Yes | 1 | 371.75 | 1133.39 | 3.0488 | 169.1902 | 47.17 | 1.3935 | 266.7653 | 27.3936 | 60.2778 |  |  | 10 |  | 2667.6532 |  | 1.9479
BLD1PRE |  | Kitchen | Yes | 1 | 139.41 | 425.02 | 3.0487 | 106.5301 | 0 | 18.5806 | 7.503 | 16.3771 | 376.7365 | 1198.345 | 503.4582 | 8 |  | 60.0238 | 1887.788 | 2.3617
BLD1PRE | Total | Total Conditioned Zones |  |  | 511.16 | 1558.41 |  | 275.7203 | 47.17 |  | 196.056 | 24.389 | 146.5864 | 326.8278 | 503.4582 | 9.4545 | 5.3362 | 5.3362 |  | 2.0608
BLD1PST |  | Dining | Yes | 1 | 371.75 | 1133.39 | 3.0488 | 169.1902 | 47.17 | 1.3935 | 266.7653 | 27.3936 | 60.2778 |  |  | 10 |  | 2667.6532 |  | 1.9479
BLD1PST |  | Kitchen | Yes | 1 | 139.41 | 425.02 | 3.0487 | 106.5301 | 0 | 18.5806 | 7.503 | 16.3771 | 376.7365 | 1198.345 | 503.4582 | 8 |  | 60.0238 | 1887.788 | 2.3617
BLD1PST |  | Attic | No | 1 | 511.15 | 856.26 | 1.6752 | 0 | 0 | [10 empty] | 1
BLD1PST | Total | Total Conditioned Zones |  |  | 511.16 | 1558.41 |  | 275.7203 | 47.17 |  | 196.056 | 24.389 | 146.5864 | 326.8278 | 503.4582 | 9.4545 | 5.3362 | 1956.4676 |  | 2.0608
BLD1NEW |  | Dining | Yes | 1 | 371.75 | 1133.39 | 3.0488 | 169.1902 | 47.17 | 1.3935 | 266.7653 | 22.6042 | 60.2778 |  |  | 10 |  | 2667.6532 |  | 0.51945
BLD1NEW |  | Kitchen | Yes | 1 | 139.41 | 425.02 | 3.0487 | 106.5301 | 0 | 18.5806 | 7.503 | 12.9167 | 376.7365 | 1198.345 | 503.4582 | 8 |  | 60.0238 | 1887.788 | 0.62979
BLD1NEW |  | Attic | No | 1 | 511.15 | 856.26 | 1.6752 | 0 | 0 | [10 empty] | 1
BLD1NEW | Total | Total Conditioned Zones |  |  | 511.16 | 1558.41 |  | 275.7203 | 47.17 |  | 196.056 | 19.9621 | 146.5864 | 326.8278 | 503.4582 | 9.4545 | 5.3362 | 1956.4676 |  | 0.54954

## LocationSummary
Building | UWG | Location Summary
|  |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD1PRE |  | Program
BLD1PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD1PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD1PRE |  | Fabric
BLD1PRE |  |  | Exterior walls
BLD1PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD1PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD1PRE |  |  | Roof
BLD1PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD1PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD1PRE |  |  | Window
BLD1PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD1PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD1PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD1PRE |  |  | Foundation
BLD1PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD1PRE |  |  | Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
BLD1PRE |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD1PRE |  | HVAC
BLD1PRE |  |  | HVAC Sizing
BLD1PRE | HVAC |  | Air Conditioning (kW) | 126.2887 | 130.1745 | 135.6321 | 131.72 | 114.9804 | 135.3304 | 81.2161 | 122.3538 | 113.7252 | 94.6671 | 114.4349 | 103.7584 | 113.9645 | 84.5784 | 108.9161 | 93.2676
BLD1PRE |  |  | PSZ-AC_1:1_COOLC DXCOIL | 101.7888 | 104.885 | 108.9322 | 106.1836 | 94.1844 | 108.7962 | 67.428 | 99.4679 | 89.3934 | 77.5185 | 90.4701 | 81.3397 | 86.907 | 65.3254 | 79.8101 | 67.6401
BLD1PRE |  |  | PSZ-AC_2:2_COOLC DXCOIL | 24.4999 | 25.2895 | 26.7 | 25.5364 | 20.796 | 26.5342 | 13.7881 | 22.8859 | 24.3317 | 17.1486 | 23.9648 | 22.4186 | 27.0576 | 19.253 | 29.106 | 25.6275
BLD1PRE | HEAT |  | Heating (kW) | 174.4971 | 224.2671 | 199.5291 | 239.6737 | 167.7056 | 210.7678 | 169.6649 | 251.1949 | 214.0258 | 206.3555 | 282.7693 | 235.9525 | 310.1068 | 288.8506 | 316.885 | 446.7323
BLD1PRE |  |  | PSZ-AC_1:1_HEATC | 136.2995 | 172.2158 | 153.1645 | 182.9757 | 133.9845 | 160.9575 | 138.4728 | 194.6307 | 162.2912 | 165.0986 | 213.5755 | 178.9307 | 225.6783 | 206.7285 | 223.9235 | 294.6792
BLD1PRE |  |  | PSZ-AC_2:2_HEATC | 38.1976 | 52.0513 | 46.3646 | 56.6981 | 33.7212 | 49.8103 | 31.1922 | 56.5642 | 51.7347 | 41.2568 | 69.1937 | 57.0218 | 84.4285 | 82.1221 | 92.9615 | 152.0531
BLD1PRE |  |  | HVAC Efficiency
BLD1PRE | COP |  | Air Conditioning (COP) | 3.2824 | 3.2825 | 3.2832 | 3.2823 | 3.2788 | 3.2829 | 3.3628 | 3.2805 | 3.2878 | 3.3097 | 3.2865 | 3.2883 | 3.2941 | 3.3455 | 3.3022 | 3.355
BLD1PRE |  |  | PSZ-AC_1:1_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3
BLD1PRE |  |  | PSZ-AC_2:2_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
BLD1PRE | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD1PRE |  |  | PSZ-AC_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD1PRE |  |  | PSZ-AC_2:2_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD1PRE |  |  | HVAC Control - Economizer
BLD1PRE |  |  | PSZ-AC_1:1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD1PRE |  |  | PSZ-AC_2:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
BLD1PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 6.98 | 7.13 | 7.36 | 7.2 | 6.55 | 7.34 | 6.11 | 6.82 | 7.31 | 6.36 | 6.5 | 6.77 | 6.48 | 6.62 | 6.27 | 7.53
BLD1PRE |  |  | DINING EXHAUST FAN | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83
BLD1PRE |  |  | KITCHEN EXHAUST FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
BLD1PRE |  |  | PSZ-AC_1:1_FAN | 4.1 | 4.22 | 4.39 | 4.28 | 3.82 | 4.38 | 3.52 | 4.01 | 4.36 | 3.69 | 3.64 | 3.9 | 3.5 | 3.57 | 3.21 | 4.09
BLD1PRE |  |  | PSZ-AC_2:2_FAN | 0.99 | 1.02 | 1.08 | 1.03 | 0.84 | 1.07 | 0.7 | 0.92 | 1.06 | 0.78 | 0.97 | 0.98 | 1.09 | 1.16 | 1.17 | 1.55
BLD1PRE |  | Utility Costs
BLD1PRE |  |  | Electric Utility Rates
BLD1PRE |  |  | Average Annual Rate ($/kWh) | 0.077279 | 0.10745 | 0.094685 | 0.10288 | 0.12397 | 0.094182 | 0.14437 | 0.06629 | 0.037429 | 0.069705 | 0.051815 | 0.037452 | 0.052149 | 0.068023 | 0.050825 | 0.08646
BLD1PRE |  |  | Total Cost ($/m2) | 69.34 | 90.73 | 81.96 | 80.04 | 86.9 | 77.52 | 97.42 | 49.56 | 28.16 | 47.68 | 37.19 | 26.9 | 34.69 | 47.35 | 32.56 | 60.88
BLD1PRE |  |  | Gas Utility Rates
BLD1PRE |  |  | Average Annual Rate ($/MJ) | 0.011467 | 0.0081839 | 0.008568 | 0.010545 | 0.0084183 | 0.0080956 | 0.0084371 | 0.0099602 | 0.007131 | 0.0083237 | 0.0087034 | 0.0071169 | 0.0079259 | 0.0085274 | 0.0079191 | 0.0041634
BLD1PRE |  |  | Total Cost ($/m2) | 21.95 | 19.53 | 19.02 | 30.15 | 18.84 | 20.15 | 23.67 | 35.77 | 21.85 | 28.85 | 36.45 | 25.69 | 39.18 | 37 | 45.38 | 31.45
BLD1PRE |  |  | Total Utility Costs
BLD1PRE |  |  | Cost Intensity ($/m2) | 91.28 | 110.26 | 100.98 | 110.19 | 105.74 | 97.67 | 121.09 | 85.33 | 50 | 76.53 | 73.63 | 52.59 | 73.87 | 84.35 | 77.94 | 92.33
BLD1PRE |  | Energy - End Uses
BLD1PRE |  |  | Electricity (kWh)
BLD1PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Cooling | 106444.4444 | 77786.1111 | 86311.1111 | 43188.8889 | 11755.5556 | 64558.3333 | 4255.5556 | 31841.6667 | 28213.8889 | 5688.8889 | 20458.3333 | 17144.4444 | 16138.8889 | 9241.6667 | 5497.2222 | 2480.5556
BLD1PRE |  |  | Interior Lighting | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500
BLD1PRE |  |  | Exterior Lighting | 22216.6667 | 22177.7778 | 22172.2222 | 22208.3333 | 22202.7778 | 22183.3333 | 22158.3333 | 22180.5556 | 22177.7778 | 22144.4444 | 22150 | 22155.5556 | 22169.4444 | 22141.6667 | 22136.1111 | 22002.7778
BLD1PRE |  |  | Interior Equipment | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778
BLD1PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Fans | 64338.8889 | 66772.2222 | 69227.7778 | 68186.1111 | 60183.3333 | 69741.6667 | 55047.2222 | 64519.4444 | 70616.6667 | 58675 | 61016.6667 | 64769.4444 | 38658.3333 | 61652.7778 | 37322.2222 | 73286.1111
BLD1PRE |  |  | Refrigeration | 18711.1111 | 17941.6667 | 17855.5556 | 17183.3333 | 17261.1111 | 17313.8889 | 16569.4444 | 16672.2222 | 16594.4444 | 16244.4444 | 16327.7778 | 16202.7778 | 16158.3333 | 15886.1111 | 15636.1111 | 15241.6667
BLD1PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Total End Uses | 458616.6667 | 431583.3333 | 442472.2222 | 397672.2222 | 358308.3333 | 420700 | 344933.3333 | 382122.2222 | 384511.1111 | 349655.5556 | 366858.3333 | 367177.7778 | 340030.5556 | 355827.7778 | 327494.4444 | 359916.6667
BLD1PRE |  |  | Gas (MJ)
BLD1PRE |  |  | Heating | 15000 | 225450 | 158220 | 436910 | 125570 | 274510 | 389790 | 787850 | 522630 | 711350 | 1071950 | 777430 | 1440390 | 1128160 | 1813340 | 2709610
BLD1PRE |  |  | Interior Equipment | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920
BLD1PRE |  |  | Water Systems | 162420 | 193490 | 175620 | 223430 | 217630 | 197140 | 243250 | 246970 | 242510 | 259220 | 267630 | 266550 | 285480 | 288730 | 314930 | 350570
BLD1PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Total End Uses | 978340 | 1219860 | 1134760 | 1461260 | 1144110 | 1272570 | 1433960 | 1835740 | 1566050 | 1771490 | 2140500 | 1844910 | 2526800 | 2217810 | 2929190 | 3861100
BLD1PRE |  |  | Total Building (MJ) | 2629350 | 2773550 | 2727660 | 2892880 | 2434020 | 2787090 | 2675720 | 3211380 | 2950290 | 3030250 | 3461200 | 3166750 | 3750910 | 3498790 | 4108170 | 5156790
BLD1PRE |  | Energy - End Use Intensities
BLD1PRE |  |  | Electricity (MJ/m2)
BLD1PRE |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Cooling (elec) | 749.6821 | 547.8431 | 607.8842 | 304.1769 | 82.7937 | 454.6806 | 29.9716 | 224.259 | 198.7088 | 40.0665 | 144.0869 | 120.7473 | 113.6653 | 65.0885 | 38.7166 | 17.4704
BLD1PRE |  |  | Interior Lighting (elec) | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569
BLD1PRE |  |  | Exterior Lighting (elec) | 156.4707 | 156.1968 | 156.1577 | 156.412 | 156.3729 | 156.2359 | 156.0599 | 156.2164 | 156.1968 | 155.962 | 156.0012 | 156.0403 | 156.1381 | 155.9425 | 155.9034 | 154.9643
BLD1PRE |  |  | Interior Equipment (elec) | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652
BLD1PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Fans (elec) | 453.1351 | 470.2729 | 487.5673 | 480.2309 | 423.8677 | 491.1865 | 387.6944 | 454.4067 | 497.3491 | 413.2446 | 429.7369 | 456.1675 | 272.2684 | 434.217 | 262.8583 | 516.1499
BLD1PRE |  |  | Refrigeration (elec) | 131.7813 | 126.3621 | 125.7556 | 121.0212 | 121.569 | 121.9407 | 116.6976 | 117.4215 | 116.8737 | 114.4087 | 114.9956 | 114.1152 | 113.8022 | 111.885 | 110.1242 | 107.3462
BLD1PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Total End Uses | 3230.0108 | 3039.6166 | 3116.3064 | 2800.7825 | 2523.5449 | 2962.9659 | 2429.3456 | 2691.2648 | 2708.0896 | 2462.6039 | 2583.7621 | 2586.0119 | 2394.8156 | 2506.0745 | 2306.5245 | 2534.8723
BLD1PRE |  |  | Gas (MJ/m2)
BLD1PRE |  |  | Heating (gas) | 29.3456 | 441.0643 | 309.5373 | 854.7589 | 245.6617 | 537.0439 | 762.5746 | 1541.3284 | 1022.4592 | 1391.6659 | 2097.1339 | 1520.943 | 2817.9399 | 2207.1016 | 3547.5692 | 5301.0075
BLD1PRE |  |  | Interior Equipment (gas) | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982
BLD1PRE |  |  | Water Systems (gas) | 317.7541 | 378.5386 | 343.5782 | 437.1124 | 425.7654 | 385.6794 | 475.8877 | 483.1654 | 474.44 | 507.131 | 523.5841 | 521.4712 | 558.5053 | 564.8635 | 616.1205 | 685.8456
BLD1PRE |  |  | Total End Uses | 1913.9978 | 2386.501 | 2220.0137 | 2858.7694 | 2238.3058 | 2489.6214 | 2805.3605 | 3591.392 | 3063.7778 | 3465.695 | 4187.6162 | 3609.3319 | 4943.363 | 4338.8633 | 5730.5879 | 7553.7513
BLD1PRE |  |  | Total Building (MJ/m2) | 5143.989 | 5426.098 | 5336.3201 | 5659.552 | 4761.8507 | 5452.5873 | 5234.7061 | 6282.6568 | 5771.8674 | 5928.2989 | 6771.3978 | 6195.3438 | 7338.1786 | 6844.9379 | 8037.1124 | 10088.6041
BLD1PRE |  | Peak Energy Demand
BLD1PRE |  |  | Electricity Peak Demand (kW)
BLD1PRE |  |  | Jan | 73.4107 | 69.1112 | 63.3482 | 56.0892 | 65.1993 | 54.5327 | 52.6313 | 53.7097 | 54.4421 | 53.0193 | 53.0708 | 53.6445 | 50.0217 | 53.0949 | 49.783 | 55.7873
BLD1PRE |  |  | Feb | 75.7466 | 65.881 | 67.3952 | 57.4022 | 64.9003 | 55.3308 | 54.8039 | 53.6032 | 54.4849 | 53.0248 | 53.0327 | 53.591 | 49.9826 | 53.2061 | 49.797 | 54.2673
BLD1PRE |  |  | Mar | 75.4894 | 71.6615 | 76.419 | 62.2054 | 62.207 | 61.9506 | 52.5983 | 61.8457 | 56.1566 | 52.996 | 53.933 | 61.1875 | 50.0509 | 53.1603 | 49.7656 | 54.3149
BLD1PRE |  |  | Apr | 79.1048 | 78.3817 | 79.5269 | 68.5281 | 68.2144 | 76.5089 | 56.5371 | 60.6985 | 67.4674 | 53.4745 | 52.8711 | 59.6624 | 53.4715 | 51.5683 | 46.3794 | 54.2146
BLD1PRE |  |  | May | 83.631 | 87.7187 | 96.6721 | 79.6586 | 64.958 | 86.1575 | 59.0017 | 71.0572 | 74.4099 | 58.7751 | 68.6836 | 68.2168 | 74.3139 | 61.3259 | 54.2047 | 53.2941
BLD1PRE |  |  | Jun | 86.8194 | 88.1974 | 105.0749 | 83.0712 | 61.6552 | 102.1094 | 60.0803 | 86.7393 | 81.3395 | 63.2421 | 80.1714 | 77.1763 | 76.6459 | 73.2574 | 63.5067 | 65.5607
BLD1PRE |  |  | Jul | 86.1392 | 90.6582 | 101.6043 | 91.0879 | 65.8609 | 99.7398 | 69.8701 | 87.8375 | 85.139 | 65.8107 | 83.016 | 77.3929 | 77.656 | 73.7394 | 70.8177 | 66.707
BLD1PRE |  |  | Aug | 87.3659 | 89.9381 | 103.1994 | 86.2835 | 72.8737 | 96.7761 | 64.0157 | 86.9989 | 78.6265 | 64.6667 | 81.6066 | 77.6657 | 76.6035 | 71.7246 | 66.8214 | 62.7419
BLD1PRE |  |  | Sep | 85.1737 | 87.86 | 94.5362 | 77.9829 | 79.1199 | 90.7106 | 71.4102 | 73.3714 | 72.4351 | 78.0804 | 70.3362 | 72.6493 | 59.9802 | 67.9891 | 54.7495 | 54.4481
BLD1PRE |  |  | Oct | 83.7059 | 80.9672 | 79.2119 | 70.9451 | 70.0305 | 76.8604 | 60.0232 | 69.7593 | 67.7491 | 57.8575 | 62.0379 | 65.2588 | 57.0055 | 57.6429 | 54.6109 | 54.4087
BLD1PRE |  |  | Nov | 79.2697 | 74.7022 | 72.9093 | 58.7496 | 64.9391 | 58.5527 | 52.8392 | 62.0599 | 54.5028 | 53.456 | 61.6851 | 53.6484 | 50.1917 | 53.1679 | 49.9048 | 54.3089
BLD1PRE |  |  | Dec | 72.9448 | 72.5046 | 61.3529 | 55.2901 | 66.3271 | 57.2288 | 52.6399 | 53.6933 | 54.4135 | 52.9991 | 53.0906 | 53.5773 | 50.0208 | 53.094 | 49.7822 | 55.9114
BLD1PRE |  |  | Time of Peak Electrical Demand
BLD1PRE |  |  | Jan | 06-JAN-12:00 | 03-JAN-12:15 | 28-JAN-18:15 | 23-JAN-18:15 | 26-JAN-12:00 | 19-JAN-16:00 | 15-JAN-17:15 | 09-JAN-07:30 | 25-JAN-17:30 | 14-JAN-07:45 | 18-JAN-07:15 | 27-JAN-17:15 | 16-JAN-07:45 | 10-JAN-07:00 | 16-JAN-07:45 | 01-JAN-11:15
BLD1PRE |  |  | Feb | 23-FEB-12:15 | 22-FEB-18:15 | 28-FEB-18:30 | 18-FEB-18:30 | 12-FEB-12:00 | 08-FEB-12:00 | 14-FEB-12:00 | 15-FEB-17:45 | 14-FEB-17:45 | 21-FEB-17:45 | 27-FEB-18:45 | 11-FEB-17:30 | 18-FEB-07:15 | 02-FEB-17:30 | 28-FEB-17:00 | 27-FEB-08:15
BLD1PRE |  |  | Mar | 13-MAR-11:00 | 25-MAR-17:15 | 17-MAR-16:15 | 28-MAR-17:15 | 30-MAR-11:00 | 31-MAR-15:00 | 22-MAR-06:15 | 09-MAR-18:30 | 25-MAR-15:45 | 13-MAR-06:30 | 14-MAR-17:00 | 26-MAR-16:30 | 23-MAR-06:15 | 09-MAR-18:30 | 18-MAR-06:15 | 09-MAR-07:30
BLD1PRE |  |  | Apr | 01-APR-17:15 | 29-APR-15:15 | 01-APR-17:15 | 14-APR-17:15 | 11-APR-16:15 | 21-APR-16:15 | 29-APR-11:00 | 05-APR-17:15 | 21-APR-17:15 | 29-APR-15:15 | 28-APR-16:15 | 24-APR-11:00 | 16-APR-17:15 | 06-APR-17:15 | 14-APR-10:15 | 01-APR-06:15
BLD1PRE |  |  | May | 23-MAY-11:00 | 26-MAY-17:30 | 28-MAY-16:00 | 31-MAY-17:30 | 29-MAY-11:00 | 31-MAY-16:15 | 09-MAY-11:00 | 31-MAY-16:15 | 31-MAY-17:15 | 15-MAY-16:00 | 30-MAY-17:15 | 23-MAY-17:15 | 27-MAY-15:15 | 16-MAY-17:15 | 31-MAY-17:15 | 30-MAY-17:15
BLD1PRE |  |  | Jun | 26-JUN-10:00 | 13-JUN-17:30 | 08-JUN-15:00 | 19-JUN-17:15 | 28-JUN-11:00 | 27-JUN-15:00 | 16-JUN-11:00 | 30-JUN-16:00 | 19-JUN-17:15 | 27-JUN-17:15 | 08-JUN-11:00 | 28-JUN-11:00 | 29-JUN-17:30 | 30-JUN-15:00 | 14-JUN-17:30 | 20-JUN-17:00
BLD1PRE |  |  | Jul | 13-JUL-11:00 | 30-JUL-15:30 | 19-JUL-16:00 | 03-JUL-16:30 | 29-JUL-10:15 | 24-JUL-16:15 | 02-JUL-15:15 | 25-JUL-10:00 | 31-JUL-17:30 | 24-JUL-17:00 | 14-JUL-11:00 | 17-JUL-16:15 | 13-JUL-17:00 | 21-JUL-16:00 | 06-JUL-17:30 | 29-JUL-17:00
BLD1PRE |  |  | Aug | 21-AUG-15:30 | 27-AUG-16:15 | 01-AUG-16:00 | 17-AUG-11:00 | 08-AUG-11:00 | 04-AUG-16:15 | 15-AUG-11:00 | 17-AUG-15:15 | 01-AUG-17:15 | 18-AUG-17:30 | 04-AUG-16:30 | 30-AUG-11:00 | 25-AUG-17:15 | 09-AUG-17:15 | 11-AUG-17:30 | 15-AUG-17:15
BLD1PRE |  |  | Sep | 06-SEP-11:00 | 16-SEP-11:00 | 12-SEP-17:15 | 11-SEP-11:00 | 24-SEP-10:00 | 01-SEP-11:00 | 28-SEP-15:30 | 05-SEP-11:00 | 20-SEP-16:00 | 02-SEP-15:00 | 06-SEP-11:15 | 02-SEP-15:15 | 14-SEP-11:00 | 01-SEP-17:15 | 08-SEP-17:00 | 19-SEP-06:30
BLD1PRE |  |  | Oct | 07-OCT-17:00 | 29-OCT-15:15 | 24-OCT-17:45 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-17:30 | 16-OCT-17:30 | 20-OCT-17:30 | 12-OCT-17:45 | 17-OCT-17:30 | 31-OCT-17:15 | 05-OCT-16:15 | 08-OCT-17:45 | 05-OCT-17:00 | 07-OCT-17:45 | 04-OCT-06:00
BLD1PRE |  |  | Nov | 01-NOV-17:45 | 27-NOV-18:15 | 12-NOV-17:30 | 19-NOV-17:30 | 20-NOV-12:00 | 10-NOV-12:00 | 02-NOV-17:30 | 04-NOV-17:15 | 09-NOV-17:15 | 04-NOV-17:30 | 02-NOV-17:30 | 04-NOV-16:00 | 03-NOV-06:30 | 21-NOV-18:00 | 08-NOV-18:45 | 14-NOV-07:00
BLD1PRE |  |  | Dec | 15-DEC-18:15 | 02-DEC-18:30 | 11-DEC-17:30 | 26-DEC-17:45 | 19-DEC-12:00 | 05-DEC-12:00 | 03-DEC-17:45 | 23-DEC-07:15 | 08-DEC-16:00 | 31-DEC-07:45 | 12-DEC-16:45 | 21-DEC-16:45 | 02-DEC-07:15 | 29-DEC-08:15 | 26-DEC-07:30 | 18-DEC-11:15
BLD1PRE |  | Source Energy
BLD1PRE |  |  | Total Source Energy (GJ) | 6544.76 | 6975.11 | 6277.51 | 6411.66 | 5241.64 | 6807.09 | 5409.15 | 6923.91 | 6303.02 | 4127.23 | 7020.61 | 6400.5 | 6966.54 | 6874.54 | 7250.83 | 8844.55
BLD1PRE |  |  | Total Source Energy (MJ/m2) | 12803.91 | 13645.83 | 12281.07 | 12543.52 | 10254.55 | 13317.12 | 10582.24 | 13545.65 | 12330.99 | 8074.36 | 13734.84 | 12521.69 | 13629.06 | 13449.07 | 14185.23 | 17303.13
BLD1PRE |  | Water Consumption (m3)
BLD1PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Water Systems | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
BLD1PRE |  |  | Total Building | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
BLD1PRE |  | Emissions
BLD1PRE |  |  | Carbon Equivalent (kg) | 143417.2118 | 165956.3603 | 154034.5689 | 148848.0627 | 62505.4708 | 164839.653 | 66169.2613 | 136220.9087 | 185311.7751 | 57411.7194 | 234189.8734 | 183260.0962 | 161955.4447 | 170026.0396 | 164920.2158 | 170901.8637
BLD1PRE |  |  | CO2 (kg) | 342210.4495 | 424788.9982 | 373241.4556 | 354152.1473 | 171404.8216 | 402373.2683 | 182333.072 | 326886.6411 | 447583.3975 | 152790.8742 | 562801.2325 | 445614.2137 | 399971.8594 | 417987.4834 | 411043.0538 | 454860.7584
BLD1PRE |  |  | NOX (kg) | 559.9062 | 532.5089 | 584.5888 | 605.9749 | 149.7892 | 611.327 | 159.928 | 549.182 | 716.2215 | 180.9933 | 922.9814 | 700.4658 | 609.1631 | 641.7616 | 610.1423 | 500.4645
BLD1PRE |  |  | SO2 (kg) | 1963.3195 | 2058.9751 | 1779.5778 | 1396.2205 | 1042.9416 | 2314.5301 | 1004.1028 | 1395.3874 | 1679.4985 | 270.7313 | 2472.9123 | 1603.8866 | 803.2064 | 950.6984 | 773.7235 | 1833.1516
BLD1PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PRE |  |  | Hg (kg) | 0.0091 | 0.0059 | 0.0049 | 0.0053 | 0.0006 | 0.0045 | 0.0006 | 0.0058 | 0.0067 | 0.0012 | 0.0077 | 0.0064 | 0.0061 | 0.0068 | 0.006 | 0.0066
BLD1PRE |  |  | Water for Electricity (m3) | 242.9552 | 702.2352 | 13143.4 | 2482.9 | 6291.1 | 11541.5 | 6056.28 | 86.7559 | 1745.98 | 3572.37 | 569.1603 | 1667.28 | 527.5389 | 22539.6 | 508.0875 | 367.7191
BLD1PST |  | Fabric
BLD1PST |  |  | Exterior walls
BLD1PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD1PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD1PST |  |  | Roof
BLD1PST | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD1PST | RvalRoof |  | R-value attic floor (m2·K / W) | 2.38 | 2.6685 | 3.8287 | 2.4461 | 1.7612 | 3.6691 | 2.0013 | 3.0365 | 2.9851 | 2.7518 | 3.323 | 3.4533 | 3.9137 | 3.5943 | 4.403 | 5.6812
BLD1PST |  |  | Window
BLD1PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD1PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD1PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD1PST |  |  | Foundation
BLD1PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD1PST |  |  | Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
BLD1PST |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD1PST |  | HVAC
BLD1PST |  |  | HVAC Sizing
BLD1PST | HVAC |  | Air Conditioning (kW) | 119.7388 | 106.524 | 106.5113 | 107.401 | 107.4206 | 104.2248 | 68.7288 | 98.12 | 90.7687 | 77.3865 | 97.4747 | 85.1657 | 94.6949 | 69.3804 | 89.3295 | 56.6415
BLD1PST |  |  | PSZ-AC_1:1_COOLC DXCOIL | 93.4702 | 84.6376 | 84.1501 | 85.0483 | 87.7991 | 82.9974 | 57.5332 | 78.2529 | 72.9748 | 64.3176 | 77.8417 | 69.3225 | 75.6585 | 55.6306 | 71.9998 | 45.0616
BLD1PST |  |  | PSZ-AC_2:2_COOLC DXCOIL | 26.2686 | 21.8863 | 22.3612 | 22.3527 | 19.6215 | 21.2274 | 11.1955 | 19.867 | 17.7939 | 13.0689 | 19.633 | 15.8433 | 19.0364 | 13.7499 | 17.3297 | 11.5799
BLD1PST | HEAT |  | Heating (kW) | 169.5488 | 198.5556 | 169.935 | 213.7145 | 159.237 | 178.7099 | 154.6386 | 224.1564 | 194.4252 | 187.5927 | 258.795 | 222.6125 | 274.942 | 258.157 | 272.3827 | 332.4583
BLD1PST |  |  | PSZ-AC_1:1_HEATC | 128.5937 | 153.5088 | 131.1048 | 164.0853 | 127.4204 | 138.8617 | 126.5176 | 175.0536 | 147.8354 | 150.0111 | 202.1085 | 169.6894 | 215.5421 | 199.5082 | 217.0335 | 263.7526
BLD1PST |  |  | PSZ-AC_2:2_HEATC | 40.9551 | 45.0468 | 38.8302 | 49.6292 | 31.8166 | 39.8482 | 28.121 | 49.1028 | 46.5898 | 37.5817 | 56.6865 | 52.9231 | 59.3999 | 58.6489 | 55.3493 | 68.7056
BLD1PST |  |  | HVAC Efficiency
BLD1PST | COP |  | Air Conditioning (COP) | 3.2892 | 3.2855 | 3.2867 | 3.2862 | 3.2793 | 3.285 | 3.3603 | 3.2847 | 3.3163 | 3.3625 | 3.2844 | 3.3688 | 3.3185 | 3.3733 | 3.3154 | 3.3756
BLD1PST |  |  | PSZ-AC_1:1_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3
BLD1PST |  |  | PSZ-AC_2:2_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD1PST | EffHeat |  | Heating Efficiency (%) | 0.78483 | 0.78454 | 0.78457 | 0.78464 | 0.784 | 0.78446 | 0.78364 | 0.78438 | 0.78479 | 0.78401 | 0.78438 | 0.78475 | 0.78432 | 0.78454 | 0.78406 | 0.78
BLD1PST |  |  | PSZ-AC_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD1PST |  |  | PSZ-AC_2:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
BLD1PST |  |  | HVAC Control - Economizer
BLD1PST |  |  | PSZ-AC_1:1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD1PST |  |  | PSZ-AC_2:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD1PST | Fan |  | Fan Max Flow Rate (m3/s ) | 6.71 | 6.18 | 6.18 | 6.21 | 6.22 | 6.08 | 5.52 | 5.84 | 6.44 | 5.63 | 5.81 | 6.22 | 5.71 | 5.93 | 5.49 | 5.31
BLD1PST |  |  | DINING EXHAUST FAN | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83
BLD1PST |  |  | KITCHEN EXHAUST FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
BLD1PST |  |  | PSZ-AC_1:1_FAN | 3.76 | 3.41 | 3.39 | 3.42 | 3.54 | 3.34 | 3 | 3.15 | 3.59 | 3.03 | 3.13 | 3.42 | 3.05 | 3.21 | 2.9 | 2.72
BLD1PST |  |  | PSZ-AC_2:2_FAN | 1.06 | 0.88 | 0.9 | 0.9 | 0.79 | 0.85 | 0.63 | 0.8 | 0.96 | 0.71 | 0.79 | 0.91 | 0.77 | 0.83 | 0.7 | 0.7
BLD1PST |  | Utility Costs
BLD1PST |  |  | Electric Utility Rates
BLD1PST |  |  | Average Annual Rate ($/kWh) | 0.077075 | 0.10688 | 0.09544 | 0.10345 | 0.12366 | 0.094009 | 0.14434 | 0.066252 | 0.037449 | 0.072238 | 0.05207 | 0.037502 | 0.051764 | 0.068028 | 0.050707 | 0.087116
BLD1PST |  |  | Total Cost ($/m2) | 68.19 | 80.73 | 73.13 | 71.98 | 85.61 | 68.36 | 89.87 | 44.48 | 27.08 | 45.22 | 34.09 | 24.58 | 33.56 | 43.43 | 31.68 | 53.65
BLD1PST |  |  | Gas Utility Rates
BLD1PST |  |  | Average Annual Rate ($/MJ) | 0.011468 | 0.0081854 | 0.0085702 | 0.01058 | 0.008414 | 0.0081023 | 0.0084333 | 0.0099789 | 0.0071503 | 0.0083189 | 0.0087359 | 0.0071323 | 0.0079332 | 0.0085664 | 0.0079269 | 0.0041689
BLD1PST |  |  | Total Cost ($/m2) | 21.99 | 19.36 | 19.04 | 29.57 | 18.53 | 20.02 | 23.58 | 34.08 | 20.53 | 28.1 | 34.35 | 24.43 | 35.29 | 34.89 | 40.31 | 28.45
BLD1PST |  |  | Total Utility Costs
BLD1PST |  |  | Cost Intensity ($/m2) | 90.17 | 100.09 | 92.17 | 101.55 | 104.14 | 88.39 | 113.45 | 78.56 | 47.61 | 73.32 | 68.44 | 49.01 | 68.85 | 78.31 | 71.98 | 82.1
BLD1PST |  | Energy - End Uses
BLD1PST |  |  | Electricity (kWh)
BLD1PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Cooling | 103127.7778 | 64413.8889 | 70072.2222 | 34358.3333 | 11572.2222 | 51372.2222 | 3163.8889 | 25441.6667 | 25677.7778 | 4316.6667 | 17397.2222 | 14694.4444 | 15097.2222 | 8519.4444 | 5141.6667 | 2033.3333
BLD1PST |  |  | Interior Lighting | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500 | 80500
BLD1PST |  |  | Exterior Lighting | 22216.6667 | 22177.7778 | 22172.2222 | 22208.3333 | 22202.7778 | 22183.3333 | 22158.3333 | 22180.5556 | 22177.7778 | 22144.4444 | 22150 | 22155.5556 | 22169.4444 | 22141.6667 | 22136.1111 | 22002.7778
BLD1PST |  |  | Interior Equipment | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778
BLD1PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Fans | 61208.3333 | 34538.8889 | 34541.6667 | 34827.7778 | 55802.7778 | 33791.6667 | 29300 | 31811.1111 | 58000 | 30183.3333 | 31636.1111 | 34852.7778 | 30825 | 32633.3333 | 29247.2222 | 28330.5556
BLD1PST |  |  | Refrigeration | 18741.6667 | 18050 | 17972.2222 | 17333.3333 | 17369.4444 | 17458.3333 | 16725 | 16861.1111 | 16805.5556 | 16438.8889 | 16527.7778 | 16438.8889 | 16377.7778 | 16116.6667 | 15883.3333 | 15508.3333
BLD1PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Total End Uses | 452197.2222 | 386086.1111 | 391663.8889 | 355633.3333 | 353855.5556 | 371711.1111 | 318252.7778 | 343200 | 369566.6667 | 319986.1111 | 334616.6667 | 335047.2222 | 331372.2222 | 326313.8889 | 319313.8889 | 314780.5556
BLD1PST |  |  | Gas (MJ)
BLD1PST |  |  | Heating | 12500 | 209590 | 154640 | 398730 | 101670 | 260120 | 379000 | 691280 | 418030 | 659640 | 934730 | 676260 | 1180050 | 984610 | 1475190 | 2327680
BLD1PST |  |  | Interior Equipment | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920
BLD1PST |  |  | Water Systems | 166550 | 198430 | 180100 | 229140 | 223190 | 202170 | 249470 | 253280 | 248710 | 265850 | 274470 | 273370 | 292790 | 296110 | 322990 | 359540
BLD1PST |  |  | Total End Uses | 979980 | 1208940 | 1135670 | 1428800 | 1125780 | 1263210 | 1429390 | 1745480 | 1467660 | 1726420 | 2010130 | 1750550 | 2273760 | 2081640 | 2599100 | 3488150
BLD1PST |  |  | Total Building (MJ) | 2607890 | 2598850 | 2545660 | 2709080 | 2399650 | 2601370 | 2575100 | 2981010 | 2798090 | 2878370 | 3214750 | 2956710 | 3466700 | 3256370 | 3748630 | 4621360
BLD1PST |  | Energy - End Use Intensities
BLD1PST |  |  | Electricity (MJ/m2)
BLD1PST |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Cooling (elec) | 726.323 | 453.6633 | 493.5146 | 241.9838 | 81.5025 | 361.8116 | 22.2831 | 179.1842 | 180.8471 | 30.402 | 122.5276 | 103.4921 | 106.3289 | 60.002 | 36.2125 | 14.3206
BLD1PST |  |  | Interior Lighting (elec) | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569 | 566.9569
BLD1PST |  |  | Exterior Lighting (elec) | 156.4707 | 156.1968 | 156.1577 | 156.412 | 156.3729 | 156.2359 | 156.0599 | 156.2164 | 156.1968 | 155.962 | 156.0012 | 156.0403 | 156.1381 | 155.9425 | 155.9034 | 154.9643
BLD1PST |  |  | Interior Equipment (elec) | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652
BLD1PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Fans (elec) | 431.0868 | 243.2554 | 243.275 | 245.29 | 393.0157 | 237.9928 | 206.3582 | 224.0438 | 408.4907 | 212.5795 | 222.8113 | 245.4661 | 217.0987 | 229.8347 | 205.9865 | 199.5305
BLD1PST |  |  | Refrigeration (elec) | 131.9965 | 127.1251 | 126.5773 | 122.0777 | 122.332 | 122.958 | 117.7932 | 118.7518 | 118.3606 | 115.7781 | 116.4042 | 115.7781 | 115.3477 | 113.5088 | 111.8654 | 109.2243
BLD1PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Total End Uses | 3184.799 | 2719.1822 | 2758.4662 | 2504.7051 | 2492.1843 | 2617.9399 | 2241.436 | 2417.1378 | 2602.8367 | 2253.6437 | 2356.6859 | 2359.7183 | 2333.8355 | 2298.2099 | 2248.9093 | 2216.9813
BLD1PST |  |  | Gas (MJ/m2)
BLD1PST |  |  | Heating (gas) | 24.4547 | 410.0362 | 302.5335 | 780.0646 | 198.9044 | 508.8917 | 741.4653 | 1352.4014 | 817.8226 | 1290.5018 | 1828.6804 | 1323.0167 | 2308.6178 | 1926.2643 | 2886.0217 | 4553.81
BLD1PST |  |  | Interior Equipment (gas) | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982
BLD1PST |  |  | Water Systems (gas) | 325.8339 | 388.2031 | 352.3428 | 448.2833 | 436.6429 | 395.5199 | 488.0563 | 495.5101 | 486.5695 | 520.1017 | 536.9657 | 534.8137 | 572.8064 | 579.3016 | 631.8889 | 703.3943
BLD1PST |  |  | Total End Uses | 1917.2063 | 2365.1374 | 2221.794 | 2795.2656 | 2202.4455 | 2471.3098 | 2796.4198 | 3414.8097 | 2871.2902 | 3377.5213 | 3932.5638 | 3424.7286 | 4448.3224 | 4072.4641 | 5084.8088 | 6824.1221
BLD1PST |  |  | Total Building (MJ/m2) | 5102.0053 | 5084.3197 | 4980.2602 | 5299.9707 | 4694.6102 | 5089.2497 | 5037.8558 | 5831.9671 | 5474.1074 | 5631.165 | 6289.2497 | 5784.4273 | 6782.1579 | 6370.674 | 7333.7181 | 9041.1034
BLD1PST |  | Peak Energy Demand
BLD1PST |  |  | Electricity Peak Demand (kW)
BLD1PST |  |  | Jan | 72.059 | 61.6613 | 56.9105 | 51.3484 | 63.3921 | 49.7316 | 49.1181 | 49.5047 | 53.443 | 49.2274 | 49.3581 | 50.2884 | 49.162 | 49.4526 | 48.912 | 50.2519
BLD1PST |  |  | Feb | 74.1711 | 59.7635 | 60.1356 | 52.2623 | 62.9863 | 49.9232 | 51.3507 | 49.4038 | 54.3024 | 49.2088 | 49.3269 | 49.8039 | 49.1276 | 49.5308 | 48.9416 | 48.687
BLD1PST |  |  | Mar | 73.9861 | 63.5801 | 66.5022 | 54.915 | 60.3664 | 53.7136 | 49.0919 | 56.5862 | 54.4783 | 49.205 | 50.3775 | 54.2856 | 49.1883 | 49.4893 | 48.8979 | 48.7286
BLD1PST |  |  | Apr | 77.6019 | 68.6831 | 69.1315 | 60.3996 | 66.1359 | 66.7971 | 50.5601 | 53.9452 | 63.3132 | 48.3091 | 47.9513 | 53.6073 | 51.6937 | 48.3169 | 45.4813 | 48.6625
BLD1PST |  |  | May | 80.9684 | 76.7249 | 82.4231 | 70.2475 | 62.4741 | 73.7092 | 52.8323 | 62.7687 | 69.1189 | 52.5238 | 61.8986 | 60.5716 | 69.1468 | 55.308 | 52.2798 | 48.079
BLD1PST |  |  | Jun | 84.3786 | 77.1755 | 89.0335 | 72.2489 | 59.8051 | 85.9295 | 54.006 | 75.2934 | 75.3012 | 56.4505 | 72.1472 | 68.1723 | 71.5692 | 65.9846 | 60.4711 | 56.8282
BLD1PST |  |  | Jul | 83.5003 | 78.7883 | 86.487 | 79.035 | 63.868 | 84.1286 | 62.2254 | 76.3696 | 77.4869 | 59.0263 | 74.4823 | 68.0545 | 72.0425 | 66.1855 | 66.6924 | 57.855
BLD1PST |  |  | Aug | 84.606 | 78.4839 | 87.7311 | 75.1232 | 70.2045 | 81.9488 | 57.0355 | 75.5331 | 73.1095 | 57.6581 | 73.2229 | 68.6889 | 71.5226 | 64.6344 | 63.4884 | 54.6582
BLD1PST |  |  | Sep | 82.5942 | 76.9116 | 81.452 | 67.7195 | 75.6455 | 77.7668 | 63.4676 | 64.1508 | 67.588 | 68.046 | 63.1884 | 63.7402 | 57.7147 | 61.2055 | 53.8467 | 48.848
BLD1PST |  |  | Oct | 82.1188 | 72.8404 | 70.666 | 63.5651 | 67.7762 | 68.4834 | 55.8133 | 63.3741 | 65.2519 | 53.6675 | 57.5027 | 57.8445 | 55.7115 | 54.4188 | 53.6236 | 48.8071
BLD1PST |  |  | Nov | 78.0384 | 68.5395 | 64.8264 | 53.0938 | 63.0519 | 51.4688 | 49.5492 | 56.8378 | 55.2424 | 49.7715 | 57.2897 | 50.7941 | 49.5087 | 49.5326 | 49.03 | 48.7243
BLD1PST |  |  | Dec | 71.9819 | 66.5307 | 55.0813 | 51.0482 | 64.383 | 50.1745 | 49.1326 | 49.4901 | 52.9796 | 49.2103 | 49.3772 | 49.7924 | 49.1597 | 49.4509 | 48.9122 | 50.3264
BLD1PST |  |  | Time of Peak Electrical Demand
BLD1PST |  |  | Jan | 06-JAN-12:15 | 20-JAN-18:15 | 28-JAN-18:15 | 23-JAN-18:15 | 26-JAN-12:00 | 18-JAN-16:00 | 15-JAN-17:15 | 09-JAN-07:30 | 25-JAN-17:30 | 14-JAN-07:45 | 18-JAN-07:15 | 27-JAN-17:15 | 16-JAN-07:45 | 10-JAN-07:00 | 16-JAN-07:45 | 01-JAN-11:15
BLD1PST |  |  | Feb | 23-FEB-12:15 | 22-FEB-18:15 | 28-FEB-18:30 | 18-FEB-18:30 | 12-FEB-12:00 | 08-FEB-17:15 | 15-FEB-18:15 | 15-FEB-17:45 | 14-FEB-17:45 | 21-FEB-18:15 | 27-FEB-18:45 | 11-FEB-17:30 | 18-FEB-07:15 | 02-FEB-17:30 | 28-FEB-17:00 | 21-FEB-08:30
BLD1PST |  |  | Mar | 13-MAR-11:00 | 25-MAR-17:30 | 17-MAR-17:15 | 28-MAR-17:30 | 30-MAR-11:00 | 30-MAR-17:00 | 22-MAR-06:15 | 09-MAR-18:00 | 01-MAR-18:30 | 13-MAR-06:30 | 14-MAR-17:00 | 26-MAR-16:45 | 23-MAR-06:15 | 09-MAR-18:30 | 18-MAR-06:15 | 09-MAR-07:30
BLD1PST |  |  | Apr | 01-APR-17:15 | 29-APR-17:15 | 01-APR-17:15 | 14-APR-17:15 | 11-APR-17:15 | 21-APR-17:15 | 29-APR-11:00 | 05-APR-17:15 | 21-APR-17:15 | 29-APR-17:15 | 28-APR-16:15 | 24-APR-11:00 | 16-APR-17:15 | 06-APR-17:15 | 14-APR-10:15 | 01-APR-06:15
BLD1PST |  |  | May | 23-MAY-11:00 | 26-MAY-17:30 | 28-MAY-16:00 | 31-MAY-17:30 | 29-MAY-11:00 | 31-MAY-17:15 | 09-MAY-11:00 | 15-MAY-17:15 | 31-MAY-17:15 | 15-MAY-17:15 | 30-MAY-17:15 | 23-MAY-17:15 | 27-MAY-17:15 | 16-MAY-17:15 | 31-MAY-17:15 | 30-MAY-17:15
BLD1PST |  |  | Jun | 26-JUN-10:00 | 13-JUN-17:30 | 08-JUN-15:00 | 19-JUN-17:15 | 28-JUN-11:00 | 27-JUN-16:15 | 16-JUN-11:00 | 30-JUN-16:00 | 19-JUN-17:15 | 27-JUN-17:45 | 08-JUN-11:00 | 28-JUN-11:00 | 29-JUN-17:30 | 30-JUN-16:15 | 14-JUN-17:30 | 20-JUN-17:00
BLD1PST |  |  | Jul | 13-JUL-11:00 | 30-JUL-15:00 | 19-JUL-16:00 | 03-JUL-17:30 | 29-JUL-10:15 | 24-JUL-16:15 | 02-JUL-15:30 | 25-JUL-10:00 | 31-JUL-17:30 | 24-JUL-17:00 | 14-JUL-11:00 | 10-JUL-17:30 | 15-JUL-15:30 | 21-JUL-16:00 | 06-JUL-17:00 | 29-JUL-17:00
BLD1PST |  |  | Aug | 21-AUG-15:30 | 27-AUG-16:15 | 01-AUG-16:00 | 14-AUG-17:15 | 08-AUG-11:00 | 04-AUG-16:30 | 15-AUG-11:00 | 17-AUG-15:15 | 01-AUG-17:15 | 07-AUG-17:15 | 04-AUG-16:15 | 30-AUG-11:00 | 25-AUG-17:15 | 09-AUG-17:15 | 11-AUG-17:30 | 15-AUG-17:15
BLD1PST |  |  | Sep | 06-SEP-11:00 | 16-SEP-11:00 | 12-SEP-17:15 | 05-SEP-17:00 | 24-SEP-10:00 | 01-SEP-11:00 | 28-SEP-15:15 | 05-SEP-11:00 | 20-SEP-17:15 | 02-SEP-15:00 | 15-SEP-17:00 | 02-SEP-15:15 | 14-SEP-11:00 | 01-SEP-17:15 | 08-SEP-17:00 | 19-SEP-06:30
BLD1PST |  |  | Oct | 07-OCT-17:00 | 29-OCT-17:45 | 24-OCT-17:45 | 21-OCT-17:00 | 19-OCT-10:00 | 03-OCT-17:30 | 16-OCT-17:30 | 20-OCT-17:30 | 12-OCT-17:45 | 17-OCT-17:30 | 31-OCT-17:15 | 05-OCT-16:15 | 08-OCT-17:45 | 05-OCT-17:00 | 07-OCT-17:45 | 04-OCT-06:00
BLD1PST |  |  | Nov | 01-NOV-17:45 | 27-NOV-18:15 | 12-NOV-17:30 | 19-NOV-17:30 | 20-NOV-12:00 | 10-NOV-16:45 | 02-NOV-17:00 | 04-NOV-17:15 | 01-NOV-17:15 | 04-NOV-17:00 | 02-NOV-17:30 | 04-NOV-17:15 | 02-NOV-17:15 | 21-NOV-18:45 | 08-NOV-18:45 | 14-NOV-08:30
BLD1PST |  |  | Dec | 15-DEC-18:15 | 02-DEC-18:00 | 11-DEC-17:30 | 04-DEC-18:45 | 19-DEC-12:00 | 05-DEC-12:00 | 03-DEC-17:45 | 23-DEC-07:15 | 08-DEC-16:00 | 31-DEC-07:45 | 12-DEC-18:45 | 21-DEC-16:45 | 02-DEC-07:15 | 29-DEC-07:00 | 26-DEC-07:30 | 18-DEC-11:15
BLD1PST |  | Source Energy
BLD1PST |  |  | Total Source Energy (GJ) | 6469.93 | 6368.32 | 5699.95 | 5867.11 | 5171.99 | 6166.02 | 5106.86 | 6324.3 | 6017.07 | 3891.95 | 6466.64 | 5913.66 | 6583.09 | 6356.51 | 6789.15 | 7856.9
BLD1PST |  |  | Total Source Energy (MJ/m2) | 12657.5 | 12458.73 | 11151.16 | 11478.19 | 10118.28 | 12062.95 | 9990.86 | 12372.61 | 11771.56 | 7614.05 | 12651.09 | 11569.24 | 12878.89 | 12435.63 | 13282.02 | 15370.92
BLD1PST |  | Water Consumption (m3)
BLD1PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Water Systems | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
BLD1PST |  |  | Total Building | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
BLD1PST |  | Emissions
BLD1PST |  |  | Carbon Equivalent (kg) | 141686.9302 | 150583.8751 | 138713.0032 | 135313.3202 | 61654.2672 | 148147.8033 | 62968.5766 | 124090.4732 | 177432.7327 | 54437.9104 | 214648.7925 | 168432.7662 | 154428.6027 | 156784.8759 | 156167.657 | 151476.3239
BLD1PST |  |  | CO2 (kg) | 338220.8411 | 386140.2481 | 337218.5769 | 323070.9885 | 169059.7188 | 362750.5699 | 173769.6885 | 298631.1984 | 428232.4303 | 145309.0803 | 516346.5431 | 410113.776 | 379955.6864 | 385807.08 | 387389.8715 | 403615.7428
BLD1PST |  |  | NOX (kg) | 552.7971 | 481.9399 | 523.6672 | 547.6876 | 147.7326 | 546.7055 | 152.5873 | 497.821 | 686.6099 | 170.6132 | 844.5941 | 642.3412 | 584.7255 | 590.7905 | 582.7493 | 442.9668
BLD1PST |  |  | SO2 (kg) | 1935.8531 | 1841.9568 | 1575.265 | 1248.6573 | 1029.9753 | 2045.0429 | 926.4606 | 1253.2893 | 1614.2136 | 247.787 | 2255.5888 | 1463.5479 | 782.7021 | 871.8541 | 754.3285 | 1603.2999
BLD1PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1PST |  |  | Hg (kg) | 0.0089 | 0.0053 | 0.0044 | 0.0047 | 0.0006 | 0.004 | 0.0006 | 0.0052 | 0.0064 | 0.0012 | 0.007 | 0.0059 | 0.006 | 0.0063 | 0.0058 | 0.0058
BLD1PST |  |  | Water for Electricity (m3) | 239.5558 | 628.2081 | 11634.2 | 2220.43 | 6212.89 | 10197.5 | 5587.81 | 77.9196 | 1678.12 | 3269.24 | 519.1381 | 1521.38 | 514.105 | 20670.1 | 495.3964 | 321.6062
BLD1NEW |  | Program
BLD1NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD1NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD1NEW |  |  | Weighting Factor | 21.72 | 253.9818 | 59.0764 | 267.6909 |  | 114.1855 | 13.8582 | 305.8982 | 13.9891 | 24.5709 | 344.1964 | 74.7018 | 74.6182 | 9.6255 | 8.8145 | 0.33091
BLD1NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD1NEW |  |  | Exterior walls
BLD1NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD1NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
BLD1NEW |  |  | Roof
BLD1NEW | TypeRoof |  | Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
BLD1NEW | RvalRoof |  | R-value attic floor (m2·K / W) | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 5.18 | 6.5229 | 6.5229 | 6.5229 | 6.5229
BLD1NEW |  |  | Window
BLD1NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD1NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD1NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD1NEW |  |  | Skylights/TDD
BLD1NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD1NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD1NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD1NEW |  |  | Foundation
BLD1NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD1NEW |  |  | Construction | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade | 4in slab-on-grade
BLD1NEW |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD1NEW |  | HVAC
BLD1NEW |  |  | HVAC Sizing
BLD1NEW | HVAC |  | Air Conditioning (kW) | 93.1753 | 93.7839 | 93.1844 | 93.258 | 76.1909 | 91.4801 | 63.4188 | 90.641 | 83.8035 | 69.0879 | 89.6696 | 81.3529 | 89.139 | 67.7901 | 79.9157 | 53.8576
BLD1NEW |  |  | PSZ-AC_1:1_COOLC DXCOIL | 74.0884 | 74.702 | 74.3682 | 73.5956 | 59.0133 | 72.4578 | 53.9183 | 72.2505 | 67.4798 | 57.0875 | 71.5232 | 66.4685 | 71.4646 | 54.6166 | 68.7668 | 44.2716
BLD1NEW |  |  | PSZ-AC_2:2_COOLC DXCOIL | 19.0869 | 19.0818 | 18.8162 | 19.6625 | 17.1776 | 19.0223 | 9.5005 | 18.3905 | 16.3237 | 12.0004 | 18.1464 | 14.8844 | 17.6743 | 13.1734 | 11.1489 | 9.586
BLD1NEW | HEAT |  | Heating (kW) | 140.4075 | 183.6129 | 155.0762 | 197.5188 | 135.874 | 165.5506 | 147.113 | 214.9739 | 185.0393 | 177.7201 | 248.7759 | 216.0424 | 266.9188 | 252.145 | 267.6036 | 319.5478
BLD1NEW |  |  | PSZ-AC_1:1_HEATC | 110.6493 | 144.3383 | 122.4017 | 153.8625 | 108.0201 | 129.8418 | 121.5692 | 169.5206 | 141.4995 | 143.2111 | 196.3816 | 165.4385 | 211.7691 | 195.955 | 214.1865 | 262.6721
BLD1NEW |  |  | PSZ-AC_2:2_HEATC | 29.7582 | 39.2745 | 32.6745 | 43.6562 | 27.8538 | 35.7087 | 25.5438 | 45.4533 | 43.5398 | 34.509 | 52.3943 | 50.6039 | 55.1497 | 56.1901 | 53.4171 | 56.8758
BLD1NEW |  |  | HVAC Efficiency
BLD1NEW | COP |  | Air Conditioning (COP) | 3.3201 | 3.3195 | 3.3188 | 3.2869 | 3.3834 | 3.3215 | 3.3554 | 3.3193 | 3.3721 | 3.3643 | 3.319 | 3.3677 | 3.3172 | 3.3719 | 3.3516 | 3.3659
BLD1NEW |  |  | PSZ-AC_1:1_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.3 | 3.23 | 3.3 | 3.23 | 3.3 | 3.3 | 3.3
BLD1NEW |  |  | PSZ-AC_2:2_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD1NEW | EffHeat |  | Heating Efficiency (%) | 0.78424 | 0.78428 | 0.78421 | 0.78442 | 0.7841 | 0.78431 | 0.78347 | 0.78423 | 0.78471 | 0.78388 | 0.78421 | 0.78468 | 0.78413 | 0.78446 | 0.78399 | 0.78356
BLD1NEW |  |  | PSZ-AC_1:1_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD1NEW |  |  | PSZ-AC_2:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD1NEW |  |  | HVAC Control - Economizer
BLD1NEW |  |  | PSZ-AC_1:1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD1NEW |  |  | PSZ-AC_2:2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD1NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 5.64 | 5.67 | 5.64 | 5.64 | 5.27 | 5.58 | 5.24 | 5.54 | 6.04 | 5.27 | 5.5 | 5.95 | 5.48 | 5.72 | 5.33 | 5.14
BLD1NEW |  |  | DINING EXHAUST FAN | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83 | 1.83
BLD1NEW |  |  | KITCHEN EXHAUST FAN | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06
BLD1NEW |  |  | PSZ-AC_1:1_FAN | 2.98 | 3.01 | 2.99 | 2.96 | 2.69 | 2.92 | 2.78 | 2.91 | 3.26 | 2.73 | 2.88 | 3.19 | 2.88 | 3.03 | 2.77 | 2.67
BLD1NEW |  |  | PSZ-AC_2:2_FAN | 0.77 | 0.77 | 0.76 | 0.79 | 0.69 | 0.77 | 0.57 | 0.74 | 0.89 | 0.65 | 0.73 | 0.87 | 0.71 | 0.8 | 0.67 | 0.58
BLD1NEW |  | Utility Costs
BLD1NEW |  |  | Electric Utility Rates
BLD1NEW |  |  | Average Annual Rate ($/kWh) | 0.076926 | 0.10668 | 0.095687 | 0.10387 | 0.1238 | 0.094057 | 0.14458 | 0.066345 | 0.037525 | 0.072253 | 0.052271 | 0.037541 | 0.051987 | 0.068189 | 0.050793 | 0.087397
BLD1NEW |  |  | Total Cost ($/m2) | 57.68 | 74.88 | 67.84 | 67.05 | 74.13 | 63.53 | 84.15 | 41.66 | 23.67 | 42.2 | 31.99 | 23.06 | 31.61 | 40.82 | 29.74 | 50.33
BLD1NEW |  |  | Gas Utility Rates
BLD1NEW |  |  | Average Annual Rate ($/MJ) | 0.011468 | 0.0081861 | 0.0085715 | 0.01059 | 0.008418 | 0.0081051 | 0.0084323 | 0.0099821 | 0.0071459 | 0.0083176 | 0.0087421 | 0.0071351 | 0.0079327 | 0.0085764 | 0.0079269 | 0.0041722
BLD1NEW |  |  | Total Cost ($/m2) | 21.93 | 19.17 | 18.9 | 29.18 | 18.83 | 19.83 | 23.28 | 33.58 | 20.91 | 27.68 | 33.73 | 24.04 | 34.48 | 34.19 | 39.22 | 27.25
BLD1NEW |  |  | Total Utility Costs
BLD1NEW |  |  | Cost Intensity ($/m2) | 79.61 | 94.06 | 86.75 | 96.23 | 92.96 | 83.36 | 107.44 | 75.25 | 44.57 | 69.89 | 65.72 | 47.1 | 66.08 | 75.01 | 68.97 | 77.57
BLD1NEW |  | Energy - End Uses
BLD1NEW |  |  | Electricity (kWh)
BLD1NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Cooling | 83427.7778 | 59480.5556 | 63355.5556 | 31441.6667 | 10477.7778 | 47263.8889 | 2811.1111 | 23858.3333 | 21263.8889 | 3950 | 16330.5556 | 13936.1111 | 14488.8889 | 8166.6667 | 4705.5556 | 1733.3333
BLD1NEW |  |  | Interior Lighting | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222 | 65897.2222
BLD1NEW |  |  | Exterior Lighting | 18516.6667 | 18483.3333 | 18480.5556 | 18511.1111 | 18508.3333 | 18488.8889 | 18469.4444 | 18488.8889 | 18483.3333 | 18458.3333 | 18461.1111 | 18466.6667 | 18477.7778 | 18455.5556 | 18450 | 18338.8889
BLD1NEW |  |  | Interior Equipment | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778 | 166402.7778
BLD1NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Fans | 30211.1111 | 30405.5556 | 30211.1111 | 30244.4444 | 27325 | 29663.8889 | 27091.6667 | 29386.1111 | 33452.7778 | 27300 | 29072.2222 | 32705.5556 | 29002.7778 | 30819.4444 | 27811.1111 | 26275
BLD1NEW |  |  | Refrigeration | 18819.4444 | 18127.7778 | 18063.8889 | 17438.8889 | 17480.5556 | 17561.1111 | 16850 | 16966.6667 | 16911.1111 | 16552.7778 | 16663.8889 | 16575 | 16516.6667 | 16263.8889 | 16055.5556 | 15691.6667
BLD1NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Total End Uses | 383277.7778 | 358797.2222 | 362411.1111 | 329936.1111 | 306088.8889 | 345280.5556 | 297522.2222 | 321002.7778 | 322411.1111 | 298558.3333 | 312827.7778 | 313980.5556 | 310786.1111 | 306005.5556 | 299322.2222 | 294338.8889
BLD1NEW |  |  | Gas (MJ)
BLD1NEW |  |  | Heating | 13960 | 202860 | 150700 | 384170 | 124540 | 252320 | 367250 | 671850 | 451970 | 641130 | 903800 | 654850 | 1135110 | 947810 | 1413400 | 2186760
BLD1NEW |  |  | Interior Equipment | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920 | 800920
BLD1NEW |  |  | Water Systems | 162410 | 193490 | 175610 | 223430 | 217620 | 197130 | 243250 | 246970 | 242500 | 259220 | 267630 | 266550 | 285480 | 288730 | 314930 | 350570
BLD1NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Total End Uses | 977280 | 1197260 | 1127230 | 1408520 | 1143080 | 1250380 | 1411420 | 1719740 | 1495400 | 1701270 | 1972350 | 1722320 | 2221510 | 2037460 | 2529250 | 3338250
BLD1NEW |  |  | Total Building (MJ) | 2357080 | 2488940 | 2431910 | 2596290 | 2245000 | 2493390 | 2482500 | 2875350 | 2656080 | 2776080 | 3098530 | 2852660 | 3340340 | 3139080 | 3606810 | 4397870
BLD1NEW |  | Energy - End Use Intensities
BLD1NEW |  |  | Electricity (MJ/m2)
BLD1NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Cooling (elec) | 587.577 | 418.9181 | 446.2095 | 221.4418 | 73.7944 | 332.8768 | 19.7985 | 168.0329 | 149.7603 | 27.8196 | 115.0152 | 98.1512 | 102.0444 | 57.5174 | 33.141 | 12.2078
BLD1NEW |  |  | Interior Lighting (elec) | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103 | 464.1103
BLD1NEW |  |  | Exterior Lighting (elec) | 130.4118 | 130.1771 | 130.1575 | 130.3727 | 130.3531 | 130.2162 | 130.0792 | 130.2162 | 130.1771 | 130.001 | 130.0205 | 130.0597 | 130.1379 | 129.9814 | 129.9423 | 129.1597
BLD1NEW |  |  | Interior Equipment (elec) | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652 | 1171.9652
BLD1NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Fans (elec) | 212.7751 | 214.1446 | 212.7751 | 213.0099 | 192.4484 | 208.9211 | 190.805 | 206.9647 | 235.606 | 192.2723 | 204.754 | 230.3433 | 204.2649 | 217.0596 | 195.8721 | 185.0533
BLD1NEW |  |  | Refrigeration (elec) | 132.5443 | 127.6729 | 127.2229 | 122.8211 | 123.1145 | 123.6819 | 118.6736 | 119.4953 | 119.104 | 116.5803 | 117.3628 | 116.7368 | 116.3259 | 114.5456 | 113.0784 | 110.5155
BLD1NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Total End Uses | 2699.4033 | 2526.9882 | 2552.4406 | 2323.721 | 2155.7664 | 2431.7911 | 2095.4319 | 2260.8041 | 2270.7229 | 2102.7291 | 2203.228 | 2211.347 | 2188.8487 | 2155.1795 | 2108.1092 | 2073.0118
BLD1NEW |  |  | Gas (MJ/m2)
BLD1NEW |  |  | Heating (gas) | 27.311 | 396.8698 | 294.8254 | 751.5798 | 243.6467 | 493.632 | 718.4779 | 1314.3891 | 884.2219 | 1254.2893 | 1768.1698 | 1281.1308 | 2220.6984 | 1854.2698 | 2765.1374 | 4278.118
BLD1NEW |  |  | Interior Equipment (gas) | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982 | 1566.8982
BLD1NEW |  |  | Water Systems (gas) | 317.7345 | 378.5386 | 343.5586 | 437.1124 | 425.7459 | 385.6598 | 475.8877 | 483.1654 | 474.4204 | 507.131 | 523.5841 | 521.4712 | 558.5053 | 564.8635 | 616.1205 | 685.8456
BLD1NEW |  |  | Total End Uses | 1911.9241 | 2342.287 | 2205.2822 | 2755.5903 | 2236.2907 | 2446.2095 | 2761.2638 | 3364.4527 | 2925.56 | 3328.3185 | 3858.6521 | 3369.5001 | 4346.1019 | 3986.0315 | 4948.1561 | 6530.8618
BLD1NEW |  |  | Total Building (MJ/m2) | 4611.3274 | 4869.2947 | 4757.7228 | 5079.3114 | 4392.0571 | 4878.0006 | 4856.6957 | 5625.2568 | 5196.2829 | 5431.0476 | 6061.8801 | 5580.8667 | 6534.9506 | 6141.211 | 7056.2653 | 8603.8736
BLD1NEW |  | Peak Energy Demand
BLD1NEW |  |  | Electricity Peak Demand (kW)
BLD1NEW |  |  | Jan | 62.0291 | 58.092 | 52.9515 | 47.5983 | 54.0462 | 46.2873 | 45.9315 | 46.2883 | 46.8818 | 45.9519 | 46.1331 | 47.0956 | 46.0546 | 46.3433 | 45.8672 | 47.2062
BLD1NEW |  |  | Feb | 63.262 | 55.2636 | 55.8029 | 48.1215 | 53.7801 | 47.8018 | 47.8775 | 46.193 | 47.9525 | 45.93 | 46.1028 | 46.634 | 46.0216 | 46.4177 | 45.8961 | 45.6219
BLD1NEW |  |  | Mar | 63.5883 | 59.3205 | 61.8912 | 50.85 | 51.8162 | 51.1254 | 45.9119 | 52.654 | 48.0198 | 45.9311 | 47.092 | 51.2707 | 46.0801 | 47.0429 | 45.8528 | 45.6591
BLD1NEW |  |  | Apr | 65.4931 | 63.6519 | 64.1817 | 56.0243 | 55.9443 | 62.1809 | 47.7867 | 50.8411 | 55.415 | 45.5035 | 45.5899 | 51.0528 | 49.0923 | 46.0288 | 43.2818 | 45.6015
BLD1NEW |  |  | May | 68.53 | 70.3351 | 75.3865 | 65.4136 | 52.313 | 68.3746 | 50.0111 | 59.1952 | 60.8589 | 49.1518 | 58.2736 | 57.1852 | 65.4285 | 52.4092 | 49.3091 | 45.2207
BLD1NEW |  |  | Jun | 71.0159 | 70.6582 | 80.9681 | 66.6313 | 50.7785 | 78.4786 | 51.1439 | 70.4556 | 66.2845 | 52.8243 | 67.7418 | 64.9179 | 67.822 | 62.7727 | 56.7575 | 53.6751
BLD1NEW |  |  | Jul | 70.4258 | 72.5363 | 78.789 | 72.0131 | 54.2353 | 76.8911 | 57.7795 | 71.5311 | 69.1756 | 55.334 | 69.8764 | 64.8358 | 68.3761 | 63.1649 | 62.1071 | 54.7028
BLD1NEW |  |  | Aug | 70.5209 | 71.9957 | 79.8582 | 69.3568 | 59.2439 | 75.015 | 54.0416 | 70.7248 | 63.8049 | 54.1195 | 68.4676 | 65.5108 | 67.8112 | 61.6977 | 59.4369 | 51.6931
BLD1NEW |  |  | Sep | 69.6228 | 70.9145 | 74.7148 | 63.905 | 64.2359 | 71.8419 | 59.4326 | 61.4558 | 59.4806 | 63.538 | 59.9879 | 60.2169 | 55.1647 | 58.1193 | 50.8123 | 45.7728
BLD1NEW |  |  | Oct | 71.3282 | 67.9341 | 65.5846 | 58.843 | 57.9942 | 63.5296 | 51.847 | 59.0021 | 56.9894 | 50.1614 | 53.7826 | 54.7558 | 52.2778 | 51.1501 | 50.1507 | 45.7338
BLD1NEW |  |  | Nov | 67.9211 | 64.2594 | 60.0994 | 48.7868 | 53.5233 | 49.0294 | 46.3569 | 52.9285 | 48.2034 | 46.3315 | 53.5744 | 47.5723 | 46.4564 | 46.4194 | 45.9793 | 45.6556
BLD1NEW |  |  | Dec | 62.8626 | 62.1134 | 51.244 | 47.5563 | 54.7604 | 47.9079 | 45.9504 | 46.2759 | 46.7355 | 45.9356 | 46.1516 | 46.6241 | 46.0527 | 46.3422 | 45.867 | 47.2595
BLD1NEW |  |  | Time of Peak Electrical Demand
BLD1NEW |  |  | Jan | 06-JAN-12:15 | 03-JAN-12:15 | 28-JAN-18:15 | 23-JAN-18:15 | 26-JAN-12:00 | 18-JAN-16:00 | 15-JAN-17:15 | 09-JAN-07:30 | 25-JAN-17:30 | 14-JAN-07:45 | 18-JAN-07:15 | 27-JAN-17:15 | 16-JAN-07:45 | 10-JAN-07:00 | 16-JAN-07:45 | 01-JAN-11:15
BLD1NEW |  |  | Feb | 23-FEB-12:15 | 22-FEB-18:15 | 28-FEB-18:30 | 20-FEB-18:30 | 12-FEB-12:00 | 08-FEB-17:15 | 15-FEB-18:15 | 15-FEB-17:45 | 14-FEB-17:45 | 21-FEB-18:15 | 27-FEB-18:45 | 11-FEB-17:30 | 18-FEB-07:15 | 02-FEB-17:30 | 28-FEB-17:00 | 27-FEB-08:15
BLD1NEW |  |  | Mar | 13-MAR-11:00 | 25-MAR-17:30 | 17-MAR-17:15 | 28-MAR-17:30 | 04-MAR-11:00 | 30-MAR-17:00 | 22-MAR-06:15 | 09-MAR-18:00 | 01-MAR-18:15 | 13-MAR-06:30 | 14-MAR-17:00 | 26-MAR-16:30 | 23-MAR-06:15 | 30-MAR-17:15 | 13-MAR-06:30 | 09-MAR-07:30
BLD1NEW |  |  | Apr | 04-APR-17:15 | 29-APR-17:15 | 01-APR-17:15 | 14-APR-17:15 | 11-APR-17:15 | 21-APR-17:15 | 29-APR-11:00 | 05-APR-17:15 | 21-APR-17:15 | 29-APR-17:15 | 07-APR-11:00 | 24-APR-11:00 | 16-APR-17:15 | 06-APR-17:15 | 14-APR-10:15 | 01-APR-06:15
BLD1NEW |  |  | May | 23-MAY-11:15 | 26-MAY-17:30 | 28-MAY-16:00 | 31-MAY-17:45 | 29-MAY-11:00 | 31-MAY-17:15 | 09-MAY-11:00 | 15-MAY-17:15 | 31-MAY-17:15 | 15-MAY-17:15 | 30-MAY-17:15 | 23-MAY-17:15 | 27-MAY-17:15 | 16-MAY-17:15 | 31-MAY-17:15 | 30-MAY-17:15
BLD1NEW |  |  | Jun | 26-JUN-10:00 | 13-JUN-17:15 | 08-JUN-15:00 | 08-JUN-17:15 | 28-JUN-11:15 | 27-JUN-16:15 | 16-JUN-11:15 | 30-JUN-16:00 | 19-JUN-17:15 | 27-JUN-17:45 | 08-JUN-11:00 | 28-JUN-11:00 | 29-JUN-17:30 | 30-JUN-16:15 | 14-JUN-17:15 | 20-JUN-17:00
BLD1NEW |  |  | Jul | 13-JUL-10:00 | 30-JUL-10:00 | 19-JUL-16:00 | 03-JUL-17:30 | 29-JUL-10:15 | 24-JUL-16:15 | 02-JUL-15:30 | 25-JUL-10:00 | 31-JUL-17:30 | 24-JUL-17:00 | 14-JUL-11:15 | 17-JUL-11:00 | 15-JUL-15:30 | 21-JUL-16:00 | 06-JUL-17:30 | 29-JUL-17:00
BLD1NEW |  |  | Aug | 21-AUG-15:30 | 31-AUG-10:00 | 01-AUG-16:00 | 17-AUG-11:00 | 08-AUG-11:00 | 04-AUG-16:30 | 15-AUG-11:00 | 17-AUG-15:15 | 01-AUG-17:15 | 07-AUG-17:15 | 04-AUG-16:15 | 30-AUG-11:00 | 27-AUG-15:15 | 09-AUG-17:15 | 11-AUG-17:30 | 15-AUG-17:15
BLD1NEW |  |  | Sep | 06-SEP-11:00 | 16-SEP-10:00 | 12-SEP-17:30 | 11-SEP-11:00 | 24-SEP-10:00 | 01-SEP-11:00 | 28-SEP-15:15 | 05-SEP-11:00 | 20-SEP-17:15 | 02-SEP-15:00 | 06-SEP-11:15 | 02-SEP-15:15 | 14-SEP-11:00 | 01-SEP-17:15 | 08-SEP-17:00 | 19-SEP-06:30
BLD1NEW |  |  | Oct | 07-OCT-17:00 | 29-OCT-17:45 | 24-OCT-17:45 | 21-OCT-17:00 | 19-OCT-10:00 | 03-OCT-17:30 | 16-OCT-17:30 | 20-OCT-17:30 | 12-OCT-17:45 | 17-OCT-17:30 | 31-OCT-17:15 | 05-OCT-11:00 | 08-OCT-17:45 | 05-OCT-17:00 | 07-OCT-17:45 | 04-OCT-06:00
BLD1NEW |  |  | Nov | 01-NOV-17:00 | 27-NOV-18:30 | 12-NOV-17:30 | 19-NOV-17:30 | 20-NOV-12:00 | 10-NOV-17:15 | 02-NOV-17:00 | 04-NOV-17:15 | 01-NOV-17:30 | 04-NOV-17:45 | 02-NOV-17:30 | 04-NOV-17:15 | 02-NOV-17:15 | 21-NOV-07:30 | 08-NOV-18:45 | 14-NOV-08:30
BLD1NEW |  |  | Dec | 15-DEC-18:15 | 02-DEC-18:00 | 11-DEC-17:30 | 04-DEC-18:00 | 19-DEC-12:00 | 05-DEC-18:15 | 03-DEC-17:45 | 23-DEC-07:15 | 08-DEC-16:00 | 31-DEC-07:45 | 12-DEC-18:45 | 21-DEC-16:45 | 02-DEC-07:15 | 29-DEC-07:00 | 26-DEC-07:30 | 18-DEC-11:15
BLD1NEW |  | Source Energy
BLD1NEW |  |  | Total Source Energy (GJ) | 5643.98 | 5998.77 | 5357.63 | 5533.75 | 4658.69 | 5811.65 | 4856.26 | 6010.41 | 5484.12 | 3730.11 | 6147.26 | 5631.23 | 6271.32 | 6054.15 | 6465.5 | 7430.33
BLD1NEW |  |  | Total Source Energy (MJ/m2) | 11041.66 | 11735.76 | 10481.45 | 10826.01 | 9114.08 | 11369.69 | 9500.6 | 11758.52 | 10728.92 | 7297.44 | 12026.25 | 11016.71 | 12268.95 | 11844.09 | 12648.86 | 14536.4
BLD1NEW |  | Water Consumption (m3)
BLD1NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Water Systems | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
BLD1NEW |  |  | Total Building | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36 | 1377.36
BLD1NEW |  | Emissions
BLD1NEW |  |  | Carbon Equivalent (kg) | 122736.6634 | 141271.0685 | 129729.74 | 127031.5723 | 56384.2377 | 139002.1068 | 60221.9037 | 117635.6994 | 158670.7803 | 52423.7859 | 202351.4217 | 159319.1003 | 146439.978 | 148567.1428 | 148064.8667 | 143020.9054
BLD1NEW |  |  | CO2 (kg) | 294312.6379 | 362691.7444 | 316010.9198 | 304048.1961 | 155058.0692 | 340968.3413 | 166365.4608 | 283856.003 | 384794.9668 | 140291.6157 | 487576.7505 | 388593.4579 | 360988.7326 | 366244.8761 | 367974.4502 | 381396.3564
BLD1NEW |  |  | NOX (kg) | 475.4803 | 451.3663 | 488.1665 | 512.0354 | 135.7973 | 511.4738 | 146.2021 | 469.7431 | 609.1734 | 163.4671 | 794.0043 | 605.8281 | 552.6103 | 558.0621 | 550.6564 | 417.8239
BLD1NEW |  |  | SO2 (kg) | 1640.8403 | 1711.7898 | 1457.6247 | 1158.4496 | 890.9912 | 1899.6529 | 866.133 | 1172.2458 | 1408.3098 | 231.2184 | 2108.7464 | 1371.5576 | 734.1016 | 817.6198 | 707.1243 | 1499.1959
BLD1NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD1NEW |  |  | Hg (kg) | 0.0076 | 0.0049 | 0.0041 | 0.0044 | 0.0005 | 0.0037 | 0.0005 | 0.0049 | 0.0056 | 0.0011 | 0.0066 | 0.0055 | 0.0056 | 0.0059 | 0.0054 | 0.0054
BLD1NEW |  |  | Water for Electricity (m3) | 203.044 | 583.8072 | 10765.2 | 2059.98 | 5374.25 | 9472.42 | 5223.83 | 72.8795 | 1464.01 | 3050.32 | 485.3356 | 1425.73 | 482.1669 | 19383.7 | 464.3793 | 300.7199

## Picture
DOE Commercial Building Benchmark - Full Service Restaurant

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Sat |  |  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Sun |  |  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| Sat |  |  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| Sun |  |  |  | Weekday, Sat, Sun, Hol, Other | 0.45 | 0.15 | 0.15 | 0.15 | 0.15 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
SchOcc | WD | BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
| Sat |  |  |  | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
| Sun |  |  |  | Sun, Hol, Other | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
SchGas | WD | GAS_EQUIP_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
| Sat |  |  |  | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
| Sun |  |  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
|  | Kitchen_Exhaust_SCH | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
[5 empty] | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
[5 empty] | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | CLGSETP_KITCHEN_SCH | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
[5 empty] | Other | 26 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
|  | HTGSETP_KITCHEN_SCH | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
[5 empty] | WinterDesign | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
[5 empty] | Other | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  |  | Temperature | Through 12/31 | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
SetCool | WD | CLGSETP_SCH | Temperature |  | Other | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Sat |  |  |  |  | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Sun |  |  |  |  | 24 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
|  |  | Temperature | Through 12/31 | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
[5 empty] | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
SetHeat | WD | HTGSETP_SCH |  |  | Other | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| Sat |  |  |  |  | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| Sun |  |  |  |  | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  | HVACOperationSchd | On/Off | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | MinOA_Sched | Fraction | Through 12/31 | All | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
|  | Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
|  | Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
|  | Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchWater | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
| Sat |  |  |  | Sat, WinterDesign | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
| Sun |  |  |  | Sun, Hol, Other | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
|  | Kitchen Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
|  | Kitchen Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  | Kitchen Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  | Kitchen Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
|  | PlantOnSched | On/Off | Through 12/31 | All | bar: 1 to 24
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60