## 1
1 | Building Summary Large Office pre-1980 construction
UWG |  |  | PRE80 | PST80 | NEW
areaFloor |  | Total Floor Area (m2) | 46320 | 46320 | 46320
nFloor |  | Number of Floors | 12 | 12 | 12 | * Not including basement
glazing |  | Total | 0.5 | 0.5 | 0.5
hCeiling |  | Floor to Ceiling Height (m) | 3.3 | 3.3 | 3.3
areaWall |  | Gross Dimensions - Total Area (m2) | 11589.72 | 11589.72 | 11589.72
ver2hor |  | Wall to Skin Ratio | 0.765 | 0.765 | 0.765
areaRoof |  | Gross Dimensions - Total Area (m2) | 3563 | 3563 | 3563
areaWindow |  | Total Area (m2) | 4636.16 | 4636.16 | 4636.16

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD4PRE | Total | Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 1875.3935 | 9.9 | 15.7818 | 0 | 967.5482 | 10.001 | 0.83 | 23972.9872 |  | 0.53594
BLD4PST | Total | Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 1875.3935 | 9.9 | 15.7818 | 0 | 967.5482 | 10.001 | 0.83 | 23972.9872 |  | 0.53594
BLD4NEW | Total | Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 1875.3935 | 9.9 | 15.7818 | 0 | 967.5482 | 10.001 | 0.83 | 23972.9872 |  | 0.53594
24.699

## 3
3 |  | Location Summary
BUILDING | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD4PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD4PRE | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD4PRE | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD4PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD4PRE | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD4PRE | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD4PRE | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD4PRE | HVAC |  | Air Conditioning (kW) | 3891.3742 | 3811.3163 | 3744.9443 | 3752.9435 | 3227.9346 | 3390.2374 | 2895.3903 | 3750.8079 | 2890.3882 | 3088.8612 | 3338.5829 | 2506.0429 | 3306.5683 | 2467.4201 | 2864.4499 | 2546.9974
BLD4PRE | HEAT |  | HEATSYS1 BOILER | 3200.1507 | 3579.1921 | 3484.4359 | 3731.1429 | 3160.4302 | 3550.4317 | 3283.8731 | 3929.9826 | 3430.435 | 3668.9932 | 3902.7404 | 3388.2219 | 4089.5019 | 3805.6804 | 4065.4519 | 4775.9897
BLD4PRE | COP |  | COOLSYS1 CHILLER 2 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316
BLD4PRE | EffHeat |  | Heating Efficiency (%) | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
BLD4PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 250.97 | 256.3 | 277.51 | 265.88 | 247.51 | 282.05 | 246.58 | 260.65 | 287.92 | 261.26 | 231.87 | 251.31 | 234.26 | 245.89 | 229.77 | 232.89
BLD4PST | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD4PST | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD4PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD4PST | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD4PST | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD4PST | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD4PST | HVAC |  | Air Conditioning (kW) | 3525.669 | 3377.6115 | 3348.4756 | 3275.786 | 3066.2194 | 2945.2802 | 2595.5372 | 3262.4828 | 2568.4611 | 2745.9477 | 3288.0705 | 2476.546 | 3252.0781 | 2447.5331 | 3026.0508 | 2980.4652
BLD4PST | HEAT |  | HEATSYS1 BOILER | 2875.9738 | 3213.452 | 3128.9688 | 3296.8038 | 3009.0236 | 3152.3373 | 3006.6432 | 3499.2569 | 3132.4331 | 3359.3231 | 3858.6116 | 3375.4535 | 4040.4387 | 3796.3108 | 4208.4004 | 5129.4989
BLD4PST | COP |  | COOLSYS1 CHILLER 2 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316
BLD4PST | EffHeat |  | Heating Efficiency (%) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BLD4PST | Fan |  | Fan Max Flow Rate (m3/s ) | 220.71 | 222.02 | 242.94 | 223.79 | 233.33 | 241.82 | 220.68 | 220.22 | 254.09 | 231.94 | 227.66 | 249.78 | 229.59 | 244.99 | 244.06 | 271.2
BLD4NEW | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD4NEW | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD4NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD4NEW | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD4NEW | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD4NEW | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD4NEW | HVAC |  | Air Conditioning (kW) | 3193.3498 | 3063.8322 | 3034.3173 | 2870.8113 | 2410.7036 | 2501.6691 | 2371.7304 | 2973.1504 | 2264.0511 | 2402.7393 | 2956.1129 | 2202.1078 | 2926.646 | 2169.3578 | 2718.8079 | 2086.0546
BLD4NEW | HEAT |  | HEATSYS1 BOILER | 2593.1769 | 2956.4784 | 2853.4511 | 2950.0653 | 2425.2287 | 2743.5893 | 2801.3877 | 3257.6133 | 2860.0865 | 3041.7063 | 3578.3925 | 3124.1037 | 3761.7122 | 3530.4209 | 3934.498 | 4293.5769
BLD4NEW | COP |  | COOLSYS1 CHILLER 2 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316 | 3.2316
BLD4NEW | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD4NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 195.47 | 197.95 | 216.17 | 190.2 | 178.59 | 200.5 | 201.5 | 197.57 | 223.2 | 201.86 | 200.94 | 221.32 | 202.95 | 216.73 | 217.52 | 192.34
2.52

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.5 | 0.5 | 0.3 | 0.3 | 15 | 83.75 | 4366.96
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.75
| Sun |  |  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.33 | 0.2 | 0.2 | 0.1 | 0.05 | 11.3 | 60.8 | 3170.29
| Sat |  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4.3
| Sun |  |  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
SchOcc | WD |  |  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.22 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 10.2
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 3.5
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 597.6 | 3596.4 | 187526.57
| Sat |  |  |  | Sat | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 608.4
| Sun |  |  |  | Other | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 640.8
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 460.8 | 2743.2 | 143038.29
| Sat |  |  |  | Sat | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 439.2
| Sun |  |  |  | Other | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 23.5068 | 374.4
SchGas | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.37 | 29.42 | 1534.04
| Sat |  |  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.57
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.13
SchSWH | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
| Sat |  |  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
| Sun |  |  |  | Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04

## BuildingSummary
1 | Building Summary Large Office pre-1980 construction
UWG |  |  | PRE80 | PST80 | NEW
Program
|  | Building Name | Reference Building Large Office Pre-1980 | Reference Building Large Office Post-1980 | Reference Building Large Office New 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Office | Office | Office
Form
areaFloor |  | Total Floor Area (m2) | 46320 | 46320 | 46320
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 1.5 | 1.5 | 1.5
nFloor |  | Number of Floors | 12 plus basement | 12 plus basement | 12 plus basement
Window Fraction (Window to Wall Ratio)
|  | South | 0.38 | 0.38 | 0.38
|  | East | 0.38 | 0.38 | 0.38
|  | North | 0.38 | 0.38 | 0.38
|  | West | 0.38 | 0.38 | 0.38
glazing |  | Total | 0.38 | 0.38 | 0.38
|  | Skylight/TDD Percentage | 0 | 0 | 0
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | core zone with four perimeter zones on each floor | core zone with four perimeter zones on each floor | core zone with four perimeter zones on each floor
hCeiling |  | Floor to Ceiling Height (m) | 2.74 | 2.74 | 2.74
|  | Floor to Floor Height (m) | 3.96 | 3.96 | 3.96
|  | Roof type | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Mass wall | Mass wall | Mass wall
areaWall |  | Gross Dimensions - Total Area (m2) | 11589.72 | 11589.72 | 11589.72
|  | Net Dimensions - Total Area (m2) | 6953.64 | 6953.64 | 6953.64
ver2hor |  | Wall to Skin Ratio | 0.765 | 0.765 | 0.765
Roof
|  | Construction Type | IEAD | IEAD | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 3563 | 3563 | 3563
|  | Net Dimensions - Total Area (m2) | 3563 | 3563 | 3563
|  | Roof to Skin Ratio | 0.235 | 0.235 | 0.235
Window Dimensions (m2)
|  | South | 1390.85 | 1390.85 | 1390.85
|  | East | 927.23 | 927.23 | 927.23
|  | North | 1390.85 | 1390.85 | 1390.85
|  | West | 927.23 | 927.23 | 927.23
areaWindow |  | Total Area (m2) | 4636.16 | 4636.16 | 4636.16
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) | 0 | 0 | 0
|  | Operable area (m2) | 0 | 0 | 0
Foundation
|  | Foundation Type | Basement | Basement | Basement
|  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
|  | Dimensions - Total Area (m2) | 3563 | 3563 | 3563
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 8523.53 | 8523.53 | 8523.53
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 92640.76 | 92640.76 | 92640.76
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 0.36496 | 0.36496 | 0.097323
HVAC
|  | System Type | MZ-VAV | MZ-VAV | MZ-VAV
|  | Heating Type | Gas boiler | Gas boiler | Gas boiler
|  | Cooling Type | 2 water cooled chillers | 2 water cooled chillers | 2 water cooled chillers
|  | Fan Control | Variable | Variable | Variable
Service Water Heating
|  | SWH Type | boiler | boiler | boiler
|  | Fuel | gas | gas | gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 1504.13 | 1504.13 | 1504.13

## ZoneSummary
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD4PRE |  | Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 7.5347 | 10.76 |  |  | 10.001 |  | 958.9195 |  | 0
BLD4PRE |  | Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
BLD4PRE |  | Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PRE |  | Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
BLD4PRE |  | Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PRE |  | Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4PRE |  | Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
BLD4PRE |  | Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PRE |  | Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
BLD4PRE |  | Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PRE |  | Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4PRE |  | Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
BLD4PRE |  | Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PRE |  | Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
BLD4PRE |  | Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PRE |  | Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4PRE |  | Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
BLD4PRE |  | Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
BLD4PRE |  | Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 3.6267
BLD4PRE | Total | Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 2397.06 | 15.4835 | 10.76 | 0 | 967.5482 | 10.001 | 0.51755 | 23972.9872 |  | 0.25767
BLD4PST |  | Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 7.5347 | 10.76 |  |  | 10.001 |  | 958.9195 |  | 0
BLD4PST |  | Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
BLD4PST |  | Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PST |  | Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
BLD4PST |  | Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PST |  | Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4PST |  | Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
BLD4PST |  | Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PST |  | Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
BLD4PST |  | Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PST |  | Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4PST |  | Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6925 |  | 0.95205
BLD4PST |  | Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PST |  | Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 10.76 |  |  | 10.001 |  | 168.6979 |  | 0.95203
BLD4PST |  | Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 10.76 |  |  | 10.001 |  | 108.7155 |  | 0.98489
BLD4PST |  | Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 10.76 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4PST |  | Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
BLD4PST |  | Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
BLD4PST |  | Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 3.6267
BLD4PST | Total | Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 2397.06 | 15.4835 | 10.76 | 0 | 967.5482 | 10.001 |  | 23972.9872 |  | 0.25767
BLD4NEW |  | Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 10.7639 | 10.7639 |  |  | 10.001 |  | 958.9195 |  | 0
BLD4NEW |  | Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 10.7639 | 10.7639 |  |  | 10.001 |  | 168.6925 |  | 0.25388
BLD4NEW |  | Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 10.7639 | 10.7639 |  |  | 10.001 |  | 108.7155 |  | 0.26264
BLD4NEW |  | Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 10.7639 | 10.7639 |  |  | 10.001 |  | 168.6979 |  | 0.25387
BLD4NEW |  | Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 10.7639 | 10.7639 |  |  | 10.001 |  | 108.7155 |  | 0.26264
BLD4NEW |  | Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.7639 | 10.7639 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4NEW |  | Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 10.7639 | 10.7639 |  |  | 10.001 |  | 168.6925 |  | 0.25388
BLD4NEW |  | Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 10.7639 | 10.7639 |  |  | 10.001 |  | 108.7155 |  | 0.26264
BLD4NEW |  | Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 10.7639 | 10.7639 |  |  | 10.001 |  | 168.6979 |  | 0.25387
BLD4NEW |  | Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 10.7639 | 10.7639 |  |  | 10.001 |  | 108.7155 |  | 0.26264
BLD4NEW |  | Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.7639 | 10.7639 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4NEW |  | Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 10.7639 | 10.7639 |  |  | 10.001 |  | 168.6925 |  | 0.25388
BLD4NEW |  | Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 10.7639 | 10.7639 |  |  | 10.001 |  | 108.7155 |  | 0.26264
BLD4NEW |  | Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 10.7639 | 10.7639 |  |  | 10.001 |  | 168.6979 |  | 0.25387
BLD4NEW |  | Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 10.7639 | 10.7639 |  |  | 10.001 |  | 108.7155 |  | 0.26264
BLD4NEW |  | Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 10.7639 | 10.7639 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
BLD4NEW |  | Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.074437
BLD4NEW |  | Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.074437
BLD4NEW |  | Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.96713
BLD4NEW | Total | Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 2397.06 | 10.7639 | 10.7639 | 0 | 967.5482 | 10.001 |  | 23972.9872 |  | 0.068712

## LocationSummary
3 |  | Location Summary
BUILDING | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD4PRE |  | Program
BLD4PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD4PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD4PRE
BLD4PRE |  | Fabric
BLD4PRE |  |  | Exterior walls
BLD4PRE | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD4PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD4PRE |  |  | Underground walls
BLD4PRE |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD4PRE |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675
BLD4PRE |  |  | Roof
BLD4PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD4PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD4PRE |  |  | Window
BLD4PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD4PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD4PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD4PRE |  |  | Skylights/TDD
BLD4PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4PRE |  |  | Foundation
BLD4PRE |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD4PRE |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD4PRE |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD4PRE |  | HVAC
BLD4PRE |  |  | HVAC Sizing
BLD4PRE | HVAC |  | Air Conditioning (kW) | 3891.3742 | 3811.3163 | 3744.9443 | 3752.9435 | 3227.9346 | 3390.2374 | 2895.3903 | 3750.8079 | 2890.3882 | 3088.8612 | 3338.5829 | 2506.0429 | 3306.5683 | 2467.4201 | 2864.4499 | 2546.9974
BLD4PRE |  |  | COOLSYS1 CHILLER 1 | 1945.6871 | 1905.6581 | 1872.4722 | 1876.4717 | 1613.9673 | 1695.1187 | 1447.6952 | 1875.404 | 1445.1941 | 1544.4306 | 1669.2914 | 1253.0214 | 1653.2841 | 1233.71 | 1432.225 | 1273.4987
BLD4PRE |  |  | COOLSYS1 CHILLER 2 | 1945.6871 | 1905.6581 | 1872.4722 | 1876.4717 | 1613.9673 | 1695.1187 | 1447.6952 | 1875.404 | 1445.1941 | 1544.4306 | 1669.2914 | 1253.0214 | 1653.2841 | 1233.71 | 1432.225 | 1273.4987
BLD4PRE |  |  | Heating (kW)
BLD4PRE | HEAT |  | HEATSYS1 BOILER | 3200.1507 | 3579.1921 | 3484.4359 | 3731.1429 | 3160.4302 | 3550.4317 | 3283.8731 | 3929.9826 | 3430.435 | 3668.9932 | 3902.7404 | 3388.2219 | 4089.5019 | 3805.6804 | 4065.4519 | 4775.9897
BLD4PRE |  |  | HVAC Efficiency
BLD4PRE |  |  | Air Conditioning (COP)
BLD4PRE |  |  | COOLSYS1 CHILLER 1 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11
BLD4PRE | COP |  | COOLSYS1 CHILLER 2 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11
BLD4PRE | EffHeat |  | Heating Efficiency (%) | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
BLD4PRE |  |  | HVAC Control - Economizer
BLD4PRE |  |  | VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4PRE |  |  | VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4PRE |  |  | VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4PRE |  |  | VAV_5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 250.97 | 256.3 | 277.51 | 265.88 | 247.51 | 282.05 | 246.58 | 260.65 | 287.92 | 261.26 | 231.87 | 251.31 | 234.26 | 245.89 | 229.77 | 232.89
BLD4PRE |  |  | VAV_1_FAN | 19.53 | 19.89 | 21.37 | 20.63 | 19.38 | 21.84 | 19.33 | 20.35 | 22.52 | 20.36 | 17.86 | 19.43 | 18.07 | 18.99 | 17.71 | 17.84
BLD4PRE |  |  | VAV_2_FAN | 201.34 | 205.59 | 224.24 | 213.69 | 199.6 | 228.73 | 201.49 | 210.46 | 233.07 | 212.85 | 187.23 | 203.69 | 189.27 | 200.2 | 187.3 | 191.47
BLD4PRE |  |  | VAV_3_FAN | 20.58 | 21.42 | 23.78 | 22.08 | 19.4 | 23.4 | 18.72 | 20.83 | 22.65 | 20.2 | 17.85 | 18.62 | 18.01 | 17.75 | 16.81 | 16.8
BLD4PRE |  |  | VAV_5_FAN | 9.52 | 9.4 | 8.12 | 9.48 | 9.13 | 8.08 | 7.04 | 9.01 | 9.68 | 7.85 | 8.93 | 9.57 | 8.91 | 8.95 | 7.95 | 6.78
BLD4PRE |  | Utility Costs
BLD4PRE |  |  | Electric Utility Rates
BLD4PRE |  |  | Average Annual Rate ($/kWh) | 0.07924 | 0.10194 | 0.072059 | 0.094641 | 0.051424 | 0.092974 | 0.14708 | 0.064038 | 0.036955 | 0.071107 | 0.090613 | 0.036957 | 0.059144 | 0.075629 | 0.059271 | 0.096754
BLD4PRE |  |  | Total Cost ($/m2) | 16.98 | 20.56 | 14 | 18.02 | 8.87 | 16.25 | 21.93 | 11.76 | 5.69 | 10.25 | 13.77 | 5.28 | 8.84 | 10.43 | 8.11 | 12.77
BLD4PRE |  |  | Gas Utility Rates
BLD4PRE |  |  | Average Annual Rate ($/MJ) | 0.01136 | 0.0080626 | 0.0082469 | 0.0096433 | 0.0085594 | 0.0076822 | 0.0085423 | 0.0096904 | 0.0068833 | 0.0084151 | 0.0082874 | 0.0068839 | 0.0078898 | 0.008012 | 0.0078688 | 0.0041129
BLD4PRE |  |  | Total Cost ($/m2) | 0.13 | 0.43 | 0.33 | 0.97 | 0.32 | 0.44 | 0.66 | 1.63 | 0.68 | 1.48 | 1.47 | 0.78 | 1.96 | 1.47 | 2.43 | 2.27
BLD4PRE |  |  | Total Utility Costs
BLD4PRE |  |  | Cost Intensity ($/m2) | 17.11 | 20.99 | 14.33 | 18.99 | 9.19 | 16.69 | 22.59 | 13.39 | 6.37 | 11.73 | 15.24 | 6.06 | 10.8 | 11.9 | 10.54 | 15.03
BLD4PRE |  | Energy - End Uses
BLD4PRE |  |  | Electricity (kWh)
BLD4PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Cooling | 3586430.5556 | 3053255.5556 | 2675200 | 2561538.8889 | 1895033.3333 | 1892494.4444 | 966886.1111 | 2260022.2222 | 1103294.4444 | 780336.1111 | 1124527.7778 | 737386.1111 | 1020700 | 550111.1111 | 524097.2222 | 325991.6667
BLD4PRE |  |  | Interior Lighting | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444
BLD4PRE |  |  | Exterior Lighting | 269230.5556 | 269127.7778 | 269077.7778 | 269036.1111 | 268830.5556 | 268769.4444 | 268913.8889 | 268750 | 268852.7778 | 268319.4444 | 268791.6667 | 268636.1111 | 268616.6667 | 268555.5556 | 268400 | 266758.3333
BLD4PRE |  |  | Interior Equipment | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333
BLD4PRE |  |  | Exterior Equipment | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111
BLD4PRE |  |  | Fans | 242766.6667 | 228144.4444 | 281252.7778 | 229244.4444 | 199100 | 279555.5556 | 185019.4444 | 227783.3333 | 276661.1111 | 210808.3333 | 197775 | 218430.5556 | 205133.3333 | 210077.7778 | 201144.4444 | 215288.8889
BLD4PRE |  |  | Pumps | 349536.1111 | 330841.6667 | 314708.3333 | 321158.3333 | 232575 | 250550 | 154841.6667 | 326047.2222 | 161327.7778 | 122402.7778 | 143261.1111 | 112161.1111 | 131947.2222 | 91530.5556 | 83163.8889 | 62800
BLD4PRE |  |  | Heat Rejection | 273372.2222 | 255555.5556 | 253580.5556 | 237161.1111 | 191616.6667 | 199094.4444 | 126936.1111 | 220188.8889 | 117744.4444 | 91727.7778 | 102102.7778 | 80138.8889 | 95455.5556 | 62669.4444 | 55208.3333 | 37769.4444
BLD4PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Total End Uses | 9925097.2222 | 9340688.8889 | 8997583.3333 | 8821900 | 7990919.4444 | 8094227.7778 | 6906358.3333 | 8506555.5556 | 7131641.6667 | 6677358.3333 | 7040216.6667 | 6620513.8889 | 6925611.1111 | 6386705.5556 | 6335777.7778 | 6112372.2222
BLD4PRE |  |  | Gas (MJ)
BLD4PRE |  |  | Heating | 417130 | 2323930 | 1734840 | 4449210 | 1525780 | 2484270 | 3355680 | 7573800 | 4378350 | 7891170 | 7960160 | 4975620 | 11220140 | 8234880 | 14010530 | 25185950
BLD4PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Water Systems | 129190 | 163090 | 143480 | 195790 | 189530 | 167010 | 217530 | 221520 | 216650 | 234970 | 244120 | 242940 | 263660 | 267210 | 295850 | 334820
BLD4PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Total End Uses | 546320 | 2487020 | 1878310 | 4645000 | 1715310 | 2651280 | 3573210 | 7795320 | 4595000 | 8126130 | 8204290 | 5218560 | 11483800 | 8502080 | 14306380 | 25520780
BLD4PRE |  |  | Total Building (MJ) | 36276670 | 36113500 | 34269610 | 36403850 | 30482620 | 31790500 | 28436100 | 38418920 | 30268910 | 32164620 | 33549070 | 29052420 | 36416010 | 31494220 | 37115180 | 47525320
BLD4PRE |  | Energy - End Use Intensities
BLD4PRE |  |  | Electricity (MJ/m2)
BLD4PRE |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Cooling (elec) | 278.7358 | 237.2977 | 207.9154 | 199.0817 | 147.2812 | 147.0839 | 75.146 | 175.648 | 85.7476 | 60.6474 | 87.3978 | 57.3093 | 79.3284 | 42.7544 | 40.7326 | 25.3359
BLD4PRE |  |  | Interior Lighting (elec) | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522
BLD4PRE |  |  | Exterior Lighting (elec) | 20.9245 | 20.9165 | 20.9126 | 20.9094 | 20.8934 | 20.8886 | 20.8999 | 20.8871 | 20.8951 | 20.8537 | 20.8904 | 20.8783 | 20.8768 | 20.872 | 20.8599 | 20.7323
BLD4PRE |  |  | Interior Equipment (elec) | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998
BLD4PRE |  |  | Exterior Equipment (elec) | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124
BLD4PRE |  |  | Fans (elec) | 18.8677 | 17.7313 | 21.8588 | 17.8168 | 15.474 | 21.7269 | 14.3796 | 17.7032 | 21.502 | 16.3839 | 15.371 | 16.9763 | 15.9429 | 16.3272 | 15.6329 | 16.7322
BLD4PRE |  |  | Pumps (elec) | 27.1658 | 25.7129 | 24.459 | 24.9603 | 18.0756 | 19.4726 | 12.0342 | 25.3402 | 12.5383 | 9.5131 | 11.1342 | 8.7171 | 10.2549 | 7.1137 | 6.4635 | 4.8808
BLD4PRE |  |  | Heat Rejection (elec) | 21.2464 | 19.8617 | 19.7082 | 18.4321 | 14.8924 | 15.4735 | 9.8654 | 17.113 | 9.151 | 7.129 | 7.9354 | 6.2284 | 7.4188 | 4.8706 | 4.2908 | 2.9354
BLD4PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Total End Uses | 771.3743 | 725.9543 | 699.2883 | 685.6343 | 621.0508 | 629.0799 | 536.7592 | 661.1258 | 554.2681 | 518.9614 | 547.1626 | 514.5435 | 538.2555 | 496.372 | 492.4139 | 475.0509
BLD4PRE |  |  | Gas (MJ/m2)
BLD4PRE |  |  | Heating (gas) | 9.0053 | 50.1708 | 37.4531 | 96.053 | 32.9397 | 53.6323 | 72.445 | 163.509 | 94.5232 | 170.3606 | 171.8501 | 107.4175 | 242.229 | 177.7809 | 302.4701 | 543.7337
BLD4PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Water Systems (gas) | 2.7891 | 3.5209 | 3.0976 | 4.2269 | 4.0917 | 3.6055 | 4.6962 | 4.7823 | 4.6772 | 5.0727 | 5.2703 | 5.2448 | 5.6921 | 5.7687 | 6.387 | 7.2284
BLD4PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Total End Uses | 11.7944 | 53.6917 | 40.5504 | 100.2798 | 37.0314 | 57.2379 | 77.1412 | 168.2914 | 99.2004 | 175.4331 | 177.1205 | 112.6623 | 247.9211 | 183.5494 | 308.8571 | 550.9622
BLD4PRE |  |  | Total Building (MJ/m2) | 783.1687 | 779.646 | 739.8387 | 785.9143 | 658.0823 | 686.3178 | 613.9004 | 829.4172 | 653.4685 | 694.3946 | 724.2831 | 627.206 | 786.1768 | 679.9215 | 801.2711 | 1026.0132
BLD4PRE |  | Peak Energy Demand
BLD4PRE |  |  | Electricity Peak Demand (kW)
BLD4PRE |  |  | Jan | 2108.5026 | 2093.7524 | 1886.9808 | 1931.6612 | 1820.9821 | 1772.749 | 1642.2499 | 1834.58 | 1622.3343 | 1348.1928 | 1347.1568 | 1562.2106 | 1304.6889 | 1346.7153 | 1340.5254 | 1365.6017
BLD4PRE |  |  | Feb | 2112.0344 | 2042.169 | 1903.8707 | 1940.9758 | 1824.8398 | 1771.1662 | 1805.9258 | 1761.502 | 1680.2813 | 1673.9161 | 1302.2458 | 1490.1932 | 1285.4735 | 1524.7518 | 1283.3324 | 1348.5154
BLD4PRE |  |  | Mar | 2104.0368 | 2090.0104 | 1945.0387 | 2007.8454 | 1817.7147 | 1836.1657 | 1703.6358 | 2028.8426 | 1699.2332 | 1737.1676 | 1774.2187 | 1626.7205 | 1688.6073 | 1629.7202 | 1315.737 | 1345.7821
BLD4PRE |  |  | Apr | 2102.9396 | 2077.7452 | 1943.4075 | 2029.8209 | 1867.1096 | 1861.2343 | 1760.5676 | 2011.8215 | 1735.929 | 1717.0733 | 1866.2877 | 1703.9928 | 1781.8194 | 1588.1049 | 1629.3824 | 1281.2726
BLD4PRE |  |  | May | 2103.3684 | 2081.9779 | 1985.6411 | 2072.143 | 1905.3428 | 1916.6856 | 1817.2423 | 2068.8683 | 1765.0864 | 1836.2886 | 1927.3146 | 1705.7892 | 1923.9075 | 1673.1492 | 1741.7267 | 1636.8935
BLD4PRE |  |  | Jun | 2111.2775 | 2062.3722 | 2033.9645 | 2071.4295 | 1909.2588 | 1931.2056 | 1817.2172 | 2060.8004 | 2162.013 | 1833.2776 | 1944.1338 | 1867.7656 | 1934.0608 | 1742.2705 | 1837.0608 | 1755.8663
BLD4PRE |  |  | Jul | 2081.0087 | 2086.9907 | 2046.317 | 2060.2802 | 1923.2446 | 1965.9692 | 1840.8303 | 2053.6888 | 2135.0454 | 1875.2836 | 1946.262 | 1771.7732 | 1945.7341 | 1738.2398 | 1840.9591 | 1738.9608
BLD4PRE |  |  | Aug | 2089.8795 | 2068.8159 | 2057.3632 | 2071.1095 | 1922.8018 | 1953.1999 | 1829.1001 | 2093.7237 | 1862.3336 | 1865.892 | 1974.4195 | 1783.7622 | 1941.1211 | 1726.8585 | 1840.6593 | 1721.7896
BLD4PRE |  |  | Sep | 2076.606 | 2072.2165 | 2062.6587 | 2072.1033 | 1915.7379 | 1943.1162 | 1827.8132 | 2064.452 | 1818.6569 | 1839.0916 | 1956.2779 | 1714.1325 | 1946.2912 | 1729.9942 | 1800.5896 | 1611.6946
BLD4PRE |  |  | Oct | 2099.6165 | 2088.6142 | 2020.5004 | 2049.4701 | 1916.964 | 1891.75 | 1816.0282 | 2073.3877 | 1816.8187 | 1782.6555 | 1948.687 | 1670.6686 | 1825.7287 | 1671.5707 | 1669.2071 | 1342.9703
BLD4PRE |  |  | Nov | 2100.271 | 2091.6099 | 1936.657 | 1966.6995 | 1931.9904 | 1852.4207 | 1815.7522 | 2004.5172 | 1688.4359 | 1763.1416 | 1946.1226 | 1568.9529 | 1744.7596 | 1429.7016 | 1348.8875 | 1344.8503
BLD4PRE |  |  | Dec | 2102.3185 | 2093.9291 | 1933.2952 | 1955.592 | 1862.1907 | 1796.9016 | 1635.4834 | 1682.798 | 1553.029 | 1348.1584 | 1347.2143 | 1435.2416 | 1347.0197 | 1345.8675 | 1302.951 | 1347.3723
BLD4PRE |  |  | Time of Peak Electrical Demand
BLD4PRE |  |  | Jan | 05-JAN-08:09 | 20-JAN-08:09 | 26-JAN-16:10 | 24-JAN-16:00 | 25-JAN-16:40 | 18-JAN-16:49 | 06-JAN-16:10 | 09-JAN-08:00 | 26-JAN-16:19 | 02-JAN-16:49 | 12-JAN-16:00 | 27-JAN-16:10 | 02-JAN-16:00 | 05-JAN-08:09 | 13-JAN-16:00 | 02-JAN-08:09
BLD4PRE |  |  | Feb | 03-FEB-08:09 | 15-FEB-16:00 | 28-FEB-16:00 | 22-FEB-08:09 | 13-FEB-16:10 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:19 | 21-FEB-16:10 | 01-FEB-16:00 | 07-FEB-15:09 | 27-FEB-16:00 | 02-FEB-16:40 | 01-FEB-08:09 | 03-FEB-08:09
BLD4PRE |  |  | Mar | 07-MAR-08:09 | 08-MAR-08:09 | 21-MAR-15:00 | 29-MAR-15:39 | 31-MAR-15:50 | 31-MAR-15:00 | 30-MAR-15:50 | 09-MAR-16:19 | 02-MAR-16:10 | 29-MAR-15:39 | 31-MAR-15:39 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 30-MAR-07:30 | 14-MAR-07:10
BLD4PRE |  |  | Apr | 17-APR-07:10 | 17-APR-07:00 | 03-APR-15:09 | 13-APR-07:00 | 11-APR-15:09 | 10-APR-15:09 | 13-APR-15:30 | 04-APR-15:39 | 20-APR-15:00 | 19-APR-15:50 | 10-APR-07:00 | 25-APR-15:50 | 27-APR-15:09 | 06-APR-15:00 | 04-APR-15:00 | 10-APR-07:10
BLD4PRE |  |  | May | 26-MAY-07:10 | 05-MAY-07:10 | 22-MAY-07:00 | 23-MAY-07:10 | 31-MAY-07:10 | 19-MAY-07:00 | 26-MAY-15:09 | 15-MAY-07:10 | 26-MAY-15:50 | 31-MAY-15:00 | 25-MAY-15:30 | 24-MAY-15:09 | 31-MAY-07:40 | 26-MAY-15:09 | 31-MAY-15:00 | 30-MAY-15:09
BLD4PRE |  |  | Jun | 27-JUN-15:50 | 19-JUN-07:10 | 13-JUN-07:30 | 06-JUN-07:10 | 29-JUN-07:10 | 13-JUN-07:30 | 26-JUN-15:30 | 27-JUN-07:10 | 29-JUN-15:30 | 29-JUN-15:09 | 15-JUN-07:10 | 27-JUN-15:09 | 21-JUN-07:10 | 23-JUN-07:00 | 15-JUN-07:10 | 22-JUN-15:20
BLD4PRE |  |  | Jul | 13-JUL-15:39 | 18-JUL-15:00 | 13-JUL-07:10 | 24-JUL-07:10 | 20-JUL-07:10 | 28-JUL-07:10 | 03-JUL-07:40 | 25-JUL-15:30 | 07-JUL-15:00 | 31-JUL-07:00 | 17-JUL-07:00 | 25-JUL-07:10 | 17-JUL-07:10 | 21-JUL-15:50 | 05-JUL-07:00 | 24-JUL-15:00
BLD4PRE |  |  | Aug | 21-AUG-15:09 | 31-AUG-15:00 | 28-AUG-07:30 | 09-AUG-07:10 | 18-AUG-07:00 | 30-AUG-15:09 | 09-AUG-15:50 | 09-AUG-15:09 | 01-AUG-15:09 | 21-AUG-15:00 | 04-AUG-15:50 | 11-AUG-15:50 | 31-AUG-07:10 | 15-AUG-15:20 | 14-AUG-07:40 | 18-AUG-15:39
BLD4PRE |  |  | Sep | 29-SEP-07:10 | 15-SEP-15:20 | 18-SEP-07:10 | 18-SEP-07:10 | 11-SEP-07:30 | 01-SEP-15:20 | 22-SEP-15:00 | 27-SEP-07:10 | 28-SEP-15:00 | 07-SEP-15:30 | 08-SEP-07:10 | 12-SEP-15:50 | 22-SEP-07:10 | 13-SEP-15:00 | 06-SEP-15:00 | 01-SEP-15:00
BLD4PRE |  |  | Oct | 31-OCT-07:10 | 23-OCT-07:10 | 04-OCT-07:00 | 20-OCT-07:00 | 23-OCT-07:00 | 06-OCT-15:00 | 31-OCT-15:20 | 03-OCT-07:10 | 03-OCT-15:50 | 17-OCT-15:20 | 31-OCT-07:00 | 04-OCT-15:00 | 06-OCT-15:30 | 05-OCT-15:00 | 27-OCT-15:09 | 30-OCT-07:10
BLD4PRE |  |  | Nov | 15-NOV-08:09 | 20-NOV-08:09 | 06-NOV-16:00 | 22-NOV-16:10 | 09-NOV-16:00 | 10-NOV-16:40 | 16-NOV-16:00 | 03-NOV-15:00 | 08-NOV-16:10 | 03-NOV-15:09 | 02-NOV-07:00 | 10-NOV-16:10 | 02-NOV-15:39 | 21-NOV-13:00 | 09-NOV-16:40 | 06-NOV-08:09
BLD4PRE |  |  | Dec | 18-DEC-08:09 | 20-DEC-08:09 | 13-DEC-16:10 | 26-DEC-08:00 | 29-DEC-16:00 | 05-DEC-16:30 | 07-DEC-15:30 | 08-DEC-09:00 | 08-DEC-15:09 | 13-DEC-16:19 | 18-DEC-16:30 | 21-DEC-16:10 | 01-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 29-DEC-08:09
BLD4PRE |  | Source Energy
BLD4PRE |  |  | Total Source Energy (GJ) | 119114.15 | 124847.2 | 104504.8 | 111909.09 | 90907.95 | 107126.18 | 80852.6 | 118022.48 | 90203.79 | 50748.79 | 98831.69 | 84779.4 | 98232.3 | 89204.95 | 94016.41 | 106468.9
BLD4PRE |  |  | Total Source Energy (MJ/m2) | 2571.53 | 2695.3 | 2256.13 | 2415.98 | 1962.59 | 2312.72 | 1745.51 | 2547.96 | 1947.39 | 1095.6 | 2133.65 | 1830.28 | 2120.71 | 1925.83 | 2029.7 | 2298.53
BLD4PRE |  | Water Consumption (m3)
BLD4PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Heat Rejection | 29390.47 | 24493.57 | 35113.44 | 20382.02 | 14159.03 | 28761.12 | 7345.55 | 17838.36 | 15053.66 | 6228.36 | 9642.78 | 9624.33 | 8618.98 | 6634.07 | 4394.69 | 2957.86
BLD4PRE |  |  | Water Systems | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13
BLD4PRE |  |  | Total Building | 30894.6 | 25997.7 | 36617.57 | 21886.15 | 15663.17 | 30265.25 | 8849.68 | 19342.49 | 16557.8 | 7732.5 | 11146.91 | 11128.47 | 10123.11 | 8138.21 | 5898.82 | 4461.99
BLD4PRE |  | Emissions
BLD4PRE |  |  | Carbon Equivalent (kg) | 2731810 | 3160540 | 2750020 | 2801230 | 964797.0299 | 2777790 | 871551.9554 | 2436110 | 2996120 | 632875.6623 | 3901430 | 2798570 | 2577670 | 2487260 | 2426680 | 2180150
BLD4PRE |  |  | CO2 (kg) | 6331300 | 7947730 | 6485420 | 6409570 | 2582630 | 6604120 | 2341030 | 5553960 | 7027580 | 1578660 | 9087760 | 6573560 | 6063450 | 5871400 | 5745050 | 5638120
BLD4PRE |  |  | NOX (kg) | 11141.5523 | 10393.8883 | 10884.8643 | 12129.2749 | 2214.8058 | 10729.1667 | 2013.0937 | 10661.3102 | 12127.4725 | 2240.6184 | 16157.5877 | 11303.3632 | 10516.0656 | 10038.1539 | 9800.212 | 6604.8463
BLD4PRE |  |  | SO2 (kg) | 42483.5308 | 44555.7528 | 36181.5852 | 30966.1169 | 23253.0765 | 44525.4346 | 20097.6356 | 31054.4176 | 31143.6902 | 5163.242 | 47447.635 | 28911.8644 | 16348.6308 | 17055.548 | 14957.2838 | 31121.2585
BLD4PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PRE |  |  | Hg (kg) | 0.1936 | 0.1254 | 0.0983 | 0.1135 | 0.0106 | 0.0837 | 0.0094 | 0.1259 | 0.1217 | 0.0209 | 0.1438 | 0.1131 | 0.1204 | 0.1191 | 0.1106 | 0.108
BLD4PRE |  |  | Water for Electricity (m3) | 5257.9 | 15198.4 | 267268 | 55080.4 | 140303 | 222057 | 121260 | 1931.31 | 32383.4 | 68221.2 | 10922.5 | 30062.4 | 10744.7 | 404560 | 9829.58 | 6244.89
BLD4PRE |  | Location Summary
BLD4PRE |  |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD4PST |  | Program
BLD4PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD4PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD4PST
BLD4PST |  | Fabric
BLD4PST |  |  | Exterior walls
BLD4PST | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD4PST | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
BLD4PST |  |  | Underground walls
BLD4PST |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD4PST |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 1.5385 | 0.30675 | 0.30675 | 1.5385 | 1.8904 | 1.7123 | 1.8904 | 2.0661 | 2.0661 | 2.4155 | 2.2422 | 2.5974 | 3.125
BLD4PST |  |  | Roof
BLD4PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD4PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD4PST |  |  | Window
BLD4PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD4PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD4PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD4PST |  |  | Skylights/TDD
BLD4PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4PST |  |  | Foundation
BLD4PST |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD4PST |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD4PST |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD4PST |  | HVAC
BLD4PST |  |  | HVAC Sizing
BLD4PST | HVAC |  | Air Conditioning (kW) | 3525.669 | 3377.6115 | 3348.4756 | 3275.786 | 3066.2194 | 2945.2802 | 2595.5372 | 3262.4828 | 2568.4611 | 2745.9477 | 3288.0705 | 2476.546 | 3252.0781 | 2447.5331 | 3026.0508 | 2980.4652
BLD4PST |  |  | COOLSYS1 CHILLER 1 | 1762.8345 | 1688.8057 | 1674.2378 | 1637.893 | 1533.1097 | 1472.6401 | 1297.7686 | 1631.2414 | 1284.2305 | 1372.9738 | 1644.0353 | 1238.273 | 1626.0391 | 1223.7666 | 1513.0254 | 1490.2326
BLD4PST |  |  | COOLSYS1 CHILLER 2 | 1762.8345 | 1688.8057 | 1674.2378 | 1637.893 | 1533.1097 | 1472.6401 | 1297.7686 | 1631.2414 | 1284.2305 | 1372.9738 | 1644.0353 | 1238.273 | 1626.0391 | 1223.7666 | 1513.0254 | 1490.2326
BLD4PST |  |  | Heating (kW)
BLD4PST | HEAT |  | HEATSYS1 BOILER | 2875.9738 | 3213.452 | 3128.9688 | 3296.8038 | 3009.0236 | 3152.3373 | 3006.6432 | 3499.2569 | 3132.4331 | 3359.3231 | 3858.6116 | 3375.4535 | 4040.4387 | 3796.3108 | 4208.4004 | 5129.4989
BLD4PST |  |  | HVAC Efficiency
BLD4PST |  |  | Air Conditioning (COP)
BLD4PST |  |  | COOLSYS1 CHILLER 1 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
BLD4PST | COP |  | COOLSYS1 CHILLER 2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
BLD4PST | EffHeat |  | Heating Efficiency (%) | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BLD4PST |  |  | HVAC Control - Economizer
BLD4PST |  |  | VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4PST |  |  | VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4PST |  |  | VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4PST |  |  | VAV_5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4PST | Fan |  | Fan Max Flow Rate (m3/s ) | 220.71 | 222.02 | 242.94 | 223.79 | 233.33 | 241.82 | 220.68 | 220.22 | 254.09 | 231.94 | 227.66 | 249.78 | 229.59 | 244.99 | 244.06 | 271.2
BLD4PST |  |  | VAV_1_FAN | 17.27 | 17.38 | 18.83 | 17.41 | 18.38 | 18.83 | 17.29 | 16.96 | 19.86 | 18.03 | 17.52 | 19.43 | 17.66 | 18.94 | 18.77 | 20.64
BLD4PST |  |  | VAV_2_FAN | 176.53 | 178.04 | 196.39 | 178.96 | 187.79 | 195.96 | 179.31 | 176.59 | 205.37 | 188 | 182.97 | 202.34 | 184.58 | 198.82 | 198.24 | 222.54
BLD4PST |  |  | VAV_3_FAN | 17.41 | 17.24 | 19.62 | 17.37 | 18.04 | 19.01 | 16.14 | 17.05 | 18.29 | 17.3 | 17.55 | 17.45 | 17.72 | 17.3 | 18.13 | 20.22
BLD4PST |  |  | VAV_5_FAN | 9.5 | 9.36 | 8.1 | 10.05 | 9.12 | 8.02 | 7.94 | 9.62 | 10.57 | 8.61 | 9.62 | 10.56 | 9.63 | 9.93 | 8.92 | 7.8
BLD4PST |  | Utility Costs
BLD4PST |  |  | Electric Utility Rates
BLD4PST |  |  | Average Annual Rate ($/kWh) | 0.079307 | 0.1023 | 0.072102 | 0.094967 | 0.051518 | 0.092882 | 0.14661 | 0.06502 | 0.036956 | 0.070971 | 0.090651 | 0.036957 | 0.059134 | 0.07565 | 0.059356 | 0.096844
BLD4PST |  |  | Total Cost ($/m2) | 16.18 | 19.37 | 13.35 | 16.76 | 8.67 | 15.37 | 21.17 | 10.99 | 5.49 | 9.94 | 13.67 | 5.25 | 8.77 | 10.39 | 8.19 | 13.03
BLD4PST |  |  | Gas Utility Rates
BLD4PST |  |  | Average Annual Rate ($/MJ) | 0.011397 | 0.0080549 | 0.0081877 | 0.0095219 | 0.0085919 | 0.0076403 | 0.0085852 | 0.0096743 | 0.0068647 | 0.0084199 | 0.0082817 | 0.0068801 | 0.0078999 | 0.008004 | 0.0078778 | 0.0041084
BLD4PST |  |  | Total Cost ($/m2) | 0.08 | 0.41 | 0.3 | 0.78 | 0.31 | 0.42 | 0.53 | 1.12 | 0.55 | 1.01 | 1.43 | 0.78 | 1.81 | 1.34 | 2.23 | 2.17
BLD4PST |  |  | Total Utility Costs
BLD4PST |  |  | Cost Intensity ($/m2) | 16.25 | 19.78 | 13.65 | 17.55 | 8.98 | 15.8 | 21.7 | 12.12 | 6.04 | 10.95 | 15.1 | 6.04 | 10.58 | 11.73 | 10.42 | 15.2
BLD4PST |  | Energy - End Uses
BLD4PST |  |  | Electricity (kWh)
BLD4PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Cooling | 3200219.4444 | 2589358.3333 | 2359961.1111 | 2057230.5556 | 1742669.4444 | 1584555.5556 | 816433.3333 | 1749602.7778 | 943058.3333 | 663061.1111 | 1081544.4444 | 710736.1111 | 979930.5556 | 534750 | 556294.4444 | 394508.3333
BLD4PST |  |  | Interior Lighting | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444 | 2348469.4444
BLD4PST |  |  | Exterior Lighting | 269230.5556 | 269127.7778 | 269077.7778 | 269036.1111 | 268830.5556 | 268769.4444 | 268913.8889 | 268750 | 268852.7778 | 268319.4444 | 268791.6667 | 268636.1111 | 268616.6667 | 268555.5556 | 268400 | 266758.3333
BLD4PST |  |  | Interior Equipment | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333
BLD4PST |  |  | Exterior Equipment | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111
BLD4PST |  |  | Fans | 209547.2222 | 194044.4444 | 238669.4444 | 185338.8889 | 183336.1111 | 228677.7778 | 158983.3333 | 181402.7778 | 230119.4444 | 173875 | 191008.3333 | 213911.1111 | 196472.2222 | 202272.2222 | 210197.2222 | 245958.3333
BLD4PST |  |  | Pumps | 316616.6667 | 290850 | 279027.7778 | 267569.4444 | 217041.6667 | 212819.4444 | 131297.2222 | 259002.7778 | 138722.2222 | 102088.8889 | 139555.5556 | 109555.5556 | 128013.8889 | 89411.1111 | 91811.1111 | 75741.6667
BLD4PST |  |  | Heat Rejection | 247950 | 221608.3333 | 224813.8889 | 193777.7778 | 178833.3333 | 168569.4444 | 108027.7778 | 169527.7778 | 101908.3333 | 78450 | 99800 | 78191.6667 | 92933.3333 | 61569.4444 | 59311.1111 | 47066.6667
BLD4PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Total End Uses | 9447327.7778 | 8768752.7778 | 8575313.8889 | 8176713.8889 | 7794475 | 7667152.7778 | 6687419.4444 | 7832047.2222 | 6886422.2222 | 6489552.7778 | 6984458.3333 | 6584791.6667 | 6869727.7778 | 6360319.4444 | 6389775 | 6233797.2222
BLD4PST |  |  | Gas (MJ)
BLD4PST |  |  | Heating | 182280 | 2218810 | 1571300 | 3607320 | 1461480 | 2400450 | 2654670 | 5152850 | 3475460 | 5309680 | 7772920 | 5011440 | 10326050 | 7466390 | 12795370 | 24131870
BLD4PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Water Systems | 132490 | 167250 | 147150 | 200810 | 194370 | 171260 | 223090 | 227180 | 222180 | 240980 | 250380 | 249160 | 270390 | 274040 | 303430 | 343360
BLD4PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Total End Uses | 314770 | 2386060 | 1718460 | 3808130 | 1655860 | 2571710 | 2877760 | 5380040 | 3697640 | 5550660 | 8023300 | 5260600 | 10596430 | 7740430 | 13098800 | 24475230
BLD4PST |  |  | Total Building (MJ) | 34325150 | 33953580 | 32589580 | 33244300 | 29715970 | 30173460 | 26952470 | 33575400 | 28488760 | 28913060 | 33167350 | 28965850 | 35327450 | 30637580 | 36102000 | 46916900
BLD4PST |  | Energy - End Use Intensities
BLD4PST |  |  | Electricity (MJ/m2)
BLD4PST |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Cooling (elec) | 248.7197 | 201.2438 | 183.4152 | 159.8871 | 135.4395 | 123.151 | 63.4528 | 135.9784 | 73.2941 | 51.5328 | 84.0572 | 55.2381 | 76.1598 | 41.5605 | 43.235 | 30.661
BLD4PST |  |  | Interior Lighting (elec) | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522 | 182.522
BLD4PST |  |  | Exterior Lighting (elec) | 20.9245 | 20.9165 | 20.9126 | 20.9094 | 20.8934 | 20.8886 | 20.8999 | 20.8871 | 20.8951 | 20.8537 | 20.8904 | 20.8783 | 20.8768 | 20.872 | 20.8599 | 20.7323
BLD4PST |  |  | Interior Equipment (elec) | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998
BLD4PST |  |  | Exterior Equipment (elec) | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124
BLD4PST |  |  | Fans (elec) | 16.2859 | 15.0811 | 18.5493 | 14.4045 | 14.2488 | 17.7727 | 12.3561 | 14.0985 | 17.8848 | 13.5135 | 14.8451 | 16.6251 | 15.2697 | 15.7205 | 16.3364 | 19.1158
BLD4PST |  |  | Pumps (elec) | 24.6073 | 22.6047 | 21.6859 | 20.7954 | 16.8684 | 16.5402 | 10.2044 | 20.1296 | 10.7814 | 7.9343 | 10.8462 | 8.5146 | 9.9492 | 6.949 | 7.1355 | 5.8866
BLD4PST |  |  | Heat Rejection (elec) | 19.2706 | 17.2233 | 17.4724 | 15.0603 | 13.8988 | 13.1011 | 8.3959 | 13.1756 | 7.9203 | 6.0971 | 7.7564 | 6.077 | 7.2227 | 4.7852 | 4.6096 | 3.658
BLD4PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Total End Uses | 734.2422 | 681.5037 | 666.4697 | 635.4907 | 605.7832 | 595.8878 | 519.7434 | 608.7033 | 535.2098 | 504.3652 | 542.8291 | 511.7672 | 533.9123 | 494.3213 | 496.6106 | 484.488
BLD4PST |  |  | Gas (MJ/m2)
BLD4PST |  |  | Heating (gas) | 3.9352 | 47.9014 | 33.9224 | 77.8776 | 31.5516 | 51.8228 | 57.3111 | 111.2437 | 75.0309 | 114.6295 | 167.8078 | 108.1908 | 222.9267 | 161.1902 | 276.2363 | 520.9774
BLD4PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Water Systems (gas) | 2.8603 | 3.6107 | 3.1768 | 4.3352 | 4.1962 | 3.6973 | 4.8162 | 4.9045 | 4.7966 | 5.2025 | 5.4054 | 5.3791 | 5.8374 | 5.9162 | 6.5507 | 7.4127
BLD4PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Total End Uses | 6.7955 | 51.5121 | 37.0994 | 82.2128 | 35.748 | 55.5201 | 62.1273 | 116.1484 | 79.8275 | 119.8319 | 173.2132 | 113.5699 | 228.7639 | 167.1064 | 282.787 | 528.3901
BLD4PST |  |  | Purchased Cooling (MJ/m2)
BLD4PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Purchased Heating (MJ/m2)
BLD4PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Total Building (MJ/m2) | 741.0377 | 733.016 | 703.5689 | 717.7035 | 641.5312 | 651.4079 | 581.8707 | 724.8516 | 615.0373 | 624.1974 | 716.0423 | 625.3371 | 762.6762 | 661.4276 | 779.3978 | 1012.8781
BLD4PST |  | Peak Energy Demand
BLD4PST |  |  | Electricity Peak Demand (kW)
BLD4PST |  |  | Jan | 2013.7161 | 1979.8946 | 1772.272 | 1826.5606 | 1779.9603 | 1699.3036 | 1587.212 | 1748.0788 | 1564.7693 | 1339.0523 | 1345.5997 | 1553.7327 | 1303.3125 | 1345.9176 | 1344.5295 | 1370.6793
BLD4PST |  |  | Feb | 2015.4249 | 1938.8305 | 1817.3179 | 1841.0416 | 1782.4644 | 1673.5412 | 1727.3754 | 1681.2906 | 1609.5535 | 1616.0834 | 1301.4886 | 1481.6252 | 1283.7797 | 1544.3107 | 1283.5379 | 1350.3866
BLD4PST |  |  | Mar | 2011.2145 | 1977.212 | 1850.6844 | 1895.5984 | 1779.1537 | 1744.5887 | 1643.7001 | 1909.5185 | 1620.1072 | 1671.3965 | 1757.2338 | 1614.5046 | 1676.2646 | 1623.1208 | 1286.808 | 1348.8298
BLD4PST |  |  | Apr | 2005.1655 | 1971.0237 | 1861.2928 | 1917.6678 | 1829.5321 | 1759.2457 | 1686.6951 | 1895.893 | 1668.7456 | 1654.1357 | 1848.0334 | 1691.3278 | 1767.5673 | 1584.2112 | 1647.8369 | 1289.6227
BLD4PST |  |  | May | 2006.7978 | 1970.1121 | 1889.698 | 1952.2322 | 1864.1579 | 1814.1967 | 1744.5831 | 1940.7425 | 1695.6859 | 1754.7985 | 1905.2948 | 1693.1289 | 1903.159 | 1662.7982 | 1768.4941 | 1700.8225
BLD4PST |  |  | Jun | 2021.0144 | 1951.5174 | 1934.5604 | 1949.2878 | 1864.7211 | 1829.6213 | 1745.2033 | 1935.505 | 2045.9356 | 1757.7844 | 1922.8624 | 1741.7063 | 1914.4381 | 1729.8432 | 1861.6501 | 1842.5632
BLD4PST |  |  | Jul | 1990.8166 | 1990.2486 | 1941.6405 | 1935.3135 | 1878.5981 | 1850.0631 | 1771.3047 | 1940.1897 | 2041.0234 | 1796.3323 | 1924.6966 | 1758.6212 | 1923.2358 | 1720.761 | 1866.4516 | 1817.1051
BLD4PST |  |  | Aug | 1998.9559 | 1970.8295 | 1959.3915 | 1948.6811 | 1878.3378 | 1845.1602 | 1756.9011 | 1976.1421 | 1776.8794 | 1780.5795 | 1951.5778 | 1768.4362 | 1920.6505 | 1714.8324 | 1879.0611 | 1802.4823
BLD4PST |  |  | Sep | 1978.1095 | 1976.4327 | 1959.5968 | 1950.0661 | 1872.436 | 1840.3089 | 1756.3437 | 1937.7266 | 1745.0189 | 1760.133 | 1935.4963 | 1700.2511 | 1924.9965 | 1718.5074 | 1823.7652 | 1676.5179
BLD4PST |  |  | Oct | 1998.7746 | 1978.1543 | 1925.6749 | 1937.2395 | 1871.8401 | 1790.7673 | 1746.0472 | 1943.0426 | 1741.9982 | 1708.0901 | 1927.0168 | 1659.0412 | 1811.5172 | 1661.9969 | 1691.9585 | 1347.2086
BLD4PST |  |  | Nov | 2008.1002 | 1977.0149 | 1854.7638 | 1845.049 | 1890.8266 | 1759.7336 | 1751.9353 | 1886.0188 | 1619.107 | 1694.2088 | 1925.6941 | 1559.746 | 1728.7715 | 1425.0434 | 1344.5696 | 1348.4207
BLD4PST |  |  | Dec | 2007.9396 | 1980.741 | 1830.417 | 1852.0237 | 1822.8864 | 1714.9922 | 1574.098 | 1603.3883 | 1498.0493 | 1339.0895 | 1345.6529 | 1431.2269 | 1345.3253 | 1344.8562 | 1344.6171 | 1349.7297
BLD4PST |  |  | Time of Peak Electrical Demand
BLD4PST |  |  | Jan | 05-JAN-08:09 | 20-JAN-08:09 | 27-JAN-16:10 | 24-JAN-16:00 | 25-JAN-16:19 | 18-JAN-16:49 | 06-JAN-16:10 | 09-JAN-08:00 | 26-JAN-16:30 | 17-JAN-16:00 | 24-JAN-16:00 | 27-JAN-16:10 | 04-JAN-16:49 | 05-JAN-08:09 | 13-JAN-16:00 | 02-JAN-08:09
BLD4PST |  |  | Feb | 03-FEB-08:09 | 15-FEB-16:00 | 28-FEB-16:10 | 22-FEB-08:09 | 13-FEB-16:10 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:10 | 21-FEB-16:10 | 01-FEB-16:00 | 07-FEB-15:09 | 27-FEB-16:00 | 02-FEB-16:40 | 01-FEB-08:09 | 03-FEB-08:09
BLD4PST |  |  | Mar | 07-MAR-08:09 | 08-MAR-08:09 | 22-MAR-15:00 | 29-MAR-15:39 | 31-MAR-15:30 | 31-MAR-15:00 | 30-MAR-15:39 | 09-MAR-16:19 | 02-MAR-16:10 | 29-MAR-15:00 | 31-MAR-15:39 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 22-MAR-15:09 | 14-MAR-07:10
BLD4PST |  |  | Apr | 17-APR-07:10 | 17-APR-07:49 | 03-APR-15:09 | 13-APR-07:00 | 11-APR-15:09 | 21-APR-15:00 | 14-APR-15:09 | 04-APR-15:00 | 20-APR-15:00 | 19-APR-15:00 | 10-APR-07:00 | 25-APR-15:50 | 27-APR-15:09 | 06-APR-15:00 | 04-APR-15:00 | 05-APR-15:09
BLD4PST |  |  | May | 26-MAY-07:10 | 05-MAY-07:10 | 22-MAY-07:00 | 23-MAY-07:10 | 31-MAY-07:10 | 19-MAY-07:00 | 25-MAY-15:00 | 15-MAY-07:10 | 26-MAY-15:39 | 31-MAY-15:00 | 25-MAY-15:30 | 24-MAY-15:09 | 16-MAY-07:00 | 26-MAY-15:09 | 31-MAY-15:00 | 30-MAY-15:09
BLD4PST |  |  | Jun | 27-JUN-15:50 | 05-JUN-07:10 | 13-JUN-07:19 | 06-JUN-07:10 | 29-JUN-07:10 | 13-JUN-07:30 | 26-JUN-15:09 | 27-JUN-07:10 | 29-JUN-15:50 | 29-JUN-15:09 | 15-JUN-07:10 | 30-JUN-07:30 | 21-JUN-07:10 | 23-JUN-07:00 | 15-JUN-07:00 | 22-JUN-15:20
BLD4PST |  |  | Jul | 13-JUL-15:39 | 18-JUL-15:00 | 11-JUL-15:00 | 18-JUL-07:10 | 20-JUL-07:10 | 28-JUL-07:10 | 03-JUL-07:40 | 25-JUL-15:50 | 07-JUL-15:50 | 31-JUL-07:00 | 17-JUL-07:00 | 25-JUL-07:10 | 17-JUL-07:10 | 21-JUL-15:39 | 05-JUL-07:00 | 14-JUL-15:50
BLD4PST |  |  | Aug | 21-AUG-15:09 | 31-AUG-15:00 | 28-AUG-07:19 | 09-AUG-07:10 | 18-AUG-07:49 | 14-AUG-07:10 | 15-AUG-15:09 | 09-AUG-15:09 | 01-AUG-15:20 | 21-AUG-15:00 | 04-AUG-15:00 | 11-AUG-15:50 | 31-AUG-07:10 | 15-AUG-15:20 | 14-AUG-07:10 | 18-AUG-15:00
BLD4PST |  |  | Sep | 29-SEP-07:10 | 15-SEP-15:20 | 18-SEP-07:10 | 18-SEP-07:10 | 11-SEP-07:30 | 05-SEP-07:30 | 22-SEP-15:00 | 27-SEP-07:10 | 07-SEP-07:00 | 07-SEP-15:09 | 08-SEP-07:10 | 12-SEP-15:50 | 22-SEP-07:10 | 13-SEP-15:00 | 06-SEP-15:00 | 01-SEP-15:00
BLD4PST |  |  | Oct | 18-OCT-07:10 | 23-OCT-07:10 | 04-OCT-07:00 | 20-OCT-07:00 | 23-OCT-07:00 | 06-OCT-15:00 | 31-OCT-15:20 | 03-OCT-07:10 | 03-OCT-15:50 | 17-OCT-15:20 | 31-OCT-07:00 | 04-OCT-15:00 | 06-OCT-15:20 | 05-OCT-15:00 | 27-OCT-15:09 | 30-OCT-07:10
BLD4PST |  |  | Nov | 15-NOV-08:09 | 20-NOV-08:09 | 06-NOV-16:00 | 22-NOV-16:10 | 09-NOV-16:00 | 10-NOV-16:40 | 16-NOV-16:00 | 03-NOV-15:00 | 08-NOV-16:10 | 03-NOV-15:09 | 02-NOV-07:00 | 10-NOV-16:10 | 02-NOV-15:30 | 21-NOV-13:00 | 30-NOV-16:00 | 06-NOV-08:09
BLD4PST |  |  | Dec | 18-DEC-08:09 | 20-DEC-08:09 | 13-DEC-16:10 | 26-DEC-08:00 | 29-DEC-16:00 | 05-DEC-16:30 | 07-DEC-15:20 | 08-DEC-09:00 | 05-DEC-15:09 | 11-DEC-16:30 | 18-DEC-16:00 | 21-DEC-16:10 | 01-DEC-16:00 | 18-DEC-08:09 | 08-DEC-16:49 | 29-DEC-08:09
BLD4PST |  | Source Energy
BLD4PST |  |  | Total Source Energy (GJ) | 113156.17 | 117258.79 | 99521.93 | 103181.74 | 88654.24 | 101539.78 | 77653.74 | 106701.63 | 86294.76 | 46758.61 | 97922.25 | 84398.6 | 96571.81 | 88043.06 | 93365.86 | 106888.59
BLD4PST |  |  | Total Source Energy (MJ/m2) | 2442.9 | 2531.47 | 2148.56 | 2227.57 | 1913.94 | 2192.12 | 1676.45 | 2303.56 | 1863 | 1009.46 | 2114.02 | 1822.06 | 2084.87 | 1900.74 | 2015.65 | 2307.59
BLD4PST |  | Water Consumption (m3)
BLD4PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Heat Rejection | 26594.42 | 21321.3 | 31154.4 | 16727.52 | 13143.04 | 24516.89 | 6254.8 | 14310.13 | 12957.43 | 5316.18 | 9408.14 | 9385.17 | 8391.38 | 6511.92 | 4718.74 | 3650.43
BLD4PST |  |  | Water Systems | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13
BLD4PST |  |  | Total Building | 28098.56 | 22825.43 | 32658.54 | 18231.66 | 14647.18 | 26021.02 | 7758.93 | 15814.26 | 14461.56 | 6820.32 | 10912.27 | 10889.3 | 9895.51 | 8016.05 | 6222.87 | 5154.56
BLD4PST |  | Emissions
BLD4PST |  |  | Carbon Equivalent (kg) | 2596600 | 2967940 | 2619660 | 2587400 | 940767.2401 | 2632310 | 833424.4555 | 2210540 | 2879770 | 572754.3125 | 3868440 | 2784740 | 2542540 | 2463880 | 2423380 | 2195470
BLD4PST |  |  | CO2 (kg) | 6015830 | 7463760 | 6177320 | 5914910 | 2518240 | 6258820 | 2236490 | 5019940 | 6747420 | 1411990 | 9009740 | 6541750 | 5973110 | 5809290 | 5724750 | 5669240
BLD4PST |  |  | NOX (kg) | 10595.5187 | 9759.8932 | 10370.6297 | 11218.6874 | 2159.5405 | 10165.9201 | 1921.7392 | 9730.9388 | 11675.4989 | 2066.5903 | 16024.1312 | 11245.6931 | 10393.6183 | 9962.32 | 9820.8502 | 6662.6197
BLD4PST |  |  | SO2 (kg) | 40438.4304 | 41827.5968 | 34483.5095 | 28701.2841 | 22681.4313 | 42176.1694 | 19460.3567 | 28591.5446 | 30072.6199 | 5017.3935 | 47071.816 | 28755.8811 | 16216.4948 | 16984.8943 | 15084.4031 | 31739.078
BLD4PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4PST |  |  | Hg (kg) | 0.1843 | 0.1178 | 0.0937 | 0.1051 | 0.0103 | 0.0793 | 0.009 | 0.1157 | 0.1175 | 0.0201 | 0.1427 | 0.1125 | 0.1193 | 0.1185 | 0.1114 | 0.1099
BLD4PST |  |  | Water for Electricity (m3) | 5004.8 | 14267.8 | 254725 | 51052.1 | 136854 | 210341 | 117416 | 1778.17 | 31269.9 | 66302.5 | 10836 | 29900.2 | 10658 | 402889 | 9913.35 | 6368.95
BLD4NEW |  | Program
BLD4NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD4NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD4NEW |  |  | Weighting Factor | 2.7007 | 8.6441 | 1.6122 | 11.8088 |  | 7.5544 | 3.096 | 30.0394 | 0 | 4.0795 | 11.7366 | 3.2113 | 3.5332 | 0 | 0.28645 | 0
BLD4NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD4NEW |  |  | Exterior walls
BLD4NEW | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD4NEW | RvalWall |  | R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
BLD4NEW |  |  | Underground walls
BLD4NEW |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD4NEW |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 1.6313 | 1.6313
BLD4NEW |  |  | Roof
BLD4NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD4NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD4NEW |  |  | Window
BLD4NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD4NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD4NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD4NEW |  |  | Skylights/TDD
BLD4NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD4NEW |  |  | Foundation
BLD4NEW |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD4NEW |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD4NEW |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD4NEW |  | HVAC
BLD4NEW |  |  | HVAC Sizing
BLD4NEW | HVAC |  | Air Conditioning (kW) | 3193.3498 | 3063.8322 | 3034.3173 | 2870.8113 | 2410.7036 | 2501.6691 | 2371.7304 | 2973.1504 | 2264.0511 | 2402.7393 | 2956.1129 | 2202.1078 | 2926.646 | 2169.3578 | 2718.8079 | 2086.0546
BLD4NEW |  |  | COOLSYS1 CHILLER 1 | 1596.6749 | 1531.9161 | 1517.1587 | 1435.4056 | 1205.3518 | 1250.8346 | 1185.8652 | 1486.5752 | 1132.0256 | 1201.3696 | 1478.0564 | 1101.0539 | 1463.323 | 1084.6789 | 1359.404 | 1043.0273
BLD4NEW |  |  | COOLSYS1 CHILLER 2 | 1596.6749 | 1531.9161 | 1517.1587 | 1435.4056 | 1205.3518 | 1250.8346 | 1185.8652 | 1486.5752 | 1132.0256 | 1201.3696 | 1478.0564 | 1101.0539 | 1463.323 | 1084.6789 | 1359.404 | 1043.0273
BLD4NEW |  |  | Heating (kW)
BLD4NEW | HEAT |  | HEATSYS1 BOILER | 2593.1769 | 2956.4784 | 2853.4511 | 2950.0653 | 2425.2287 | 2743.5893 | 2801.3877 | 3257.6133 | 2860.0865 | 3041.7063 | 3578.3925 | 3124.1037 | 3761.7122 | 3530.4209 | 3934.498 | 4293.5769
BLD4NEW |  |  | HVAC Efficiency
BLD4NEW |  |  | Air Conditioning (COP)
BLD4NEW |  |  | COOLSYS1 CHILLER 1 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
BLD4NEW | COP |  | COOLSYS1 CHILLER 2 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
BLD4NEW | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD4NEW |  |  | HVAC Control - Economizer
BLD4NEW |  |  | VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4NEW |  |  | VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4NEW |  |  | VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4NEW |  |  | VAV_5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD4NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 195.47 | 197.95 | 216.17 | 190.2 | 178.59 | 200.5 | 201.5 | 197.57 | 223.2 | 201.86 | 200.94 | 221.32 | 202.95 | 216.73 | 217.52 | 192.34
BLD4NEW |  |  | VAV_1_FAN | 15.19 | 15.38 | 16.59 | 14.5 | 13.69 | 15.13 | 15.7 | 15.01 | 16.97 | 15.32 | 15.26 | 16.87 | 15.42 | 16.46 | 16.54 | 14.48
BLD4NEW |  |  | VAV_2_FAN | 156.58 | 158.95 | 175.09 | 152.61 | 143.72 | 162.49 | 164.61 | 159.39 | 181.24 | 164.45 | 162.37 | 180.05 | 164.13 | 176.59 | 177.06 | 156.85
BLD4NEW |  |  | VAV_3_FAN | 15.85 | 15.91 | 17.87 | 15.46 | 13.82 | 16.35 | 15.3 | 15.95 | 17.14 | 15.7 | 16.11 | 16.59 | 16.21 | 16.37 | 16.84 | 14.86
BLD4NEW |  |  | VAV_5_FAN | 7.85 | 7.71 | 6.62 | 7.63 | 7.36 | 6.53 | 5.89 | 7.22 | 7.85 | 6.39 | 7.2 | 7.81 | 7.19 | 7.31 | 7.08 | 6.15
BLD4NEW |  | Utility Costs
BLD4NEW |  |  | Electric Utility Rates
BLD4NEW |  |  | Average Annual Rate ($/kWh) | 0.078788 | 0.10202 | 0.07171 | 0.096223 | 0.050796 | 0.092422 | 0.14485 | 0.064658 | 0.036961 | 0.070376 | 0.091465 | 0.036962 | 0.058417 | 0.074933 | 0.058569 | 0.095613
BLD4NEW |  |  | Total Cost ($/m2) | 13.74 | 16.5 | 11.37 | 14.09 | 6.96 | 12.71 | 17.95 | 9.19 | 4.66 | 8.35 | 11.74 | 4.47 | 7.38 | 8.74 | 6.88 | 10.58
BLD4NEW |  |  | Gas Utility Rates
BLD4NEW |  |  | Average Annual Rate ($/MJ) | 0.011405 | 0.0080578 | 0.008192 | 0.0095713 | 0.0086094 | 0.007679 | 0.0085472 | 0.0096887 | 0.0068906 | 0.0084279 | 0.0082781 | 0.0068878 | 0.0079118 | 0.008002 | 0.0078859 | 0.0041016
BLD4NEW |  |  | Total Cost ($/m2) | 0.06 | 0.32 | 0.23 | 0.38 | 0.08 | 0.15 | 0.45 | 0.73 | 0.26 | 0.59 | 0.94 | 0.46 | 1.34 | 0.96 | 1.62 | 1.51
BLD4NEW |  |  | Total Utility Costs
BLD4NEW |  |  | Cost Intensity ($/m2) | 13.8 | 16.82 | 11.6 | 14.47 | 7.04 | 12.86 | 18.4 | 9.91 | 4.93 | 8.94 | 12.68 | 4.93 | 8.72 | 9.7 | 8.5 | 12.09
BLD4NEW |  | Energy - End Uses
BLD4NEW |  |  | Electricity (kWh)
BLD4NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Cooling | 2737244.4444 | 2218766.6667 | 2030455.5556 | 1616583.3333 | 1263455.5556 | 1231352.7778 | 726261.1111 | 1427511.1111 | 790472.2222 | 552650 | 928980.5556 | 606280.5556 | 845413.8889 | 453650 | 481461.1111 | 246855.5556
BLD4NEW |  |  | Interior Lighting | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222 | 1565647.2222
BLD4NEW |  |  | Exterior Lighting | 224066.6667 | 223980.5556 | 223938.8889 | 223902.7778 | 223733.3333 | 223680.5556 | 223800 | 223663.8889 | 223750 | 223305.5556 | 223700 | 223569.4444 | 223552.7778 | 223502.7778 | 223375 | 222008.3333
BLD4NEW |  |  | Interior Equipment | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333 | 2328883.3333
BLD4NEW |  |  | Exterior Equipment | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111
BLD4NEW |  |  | Fans | 186461.1111 | 172430.5556 | 212705.5556 | 153000 | 139333.3333 | 182291.6667 | 147269.4444 | 156155.5556 | 193555.5556 | 143677.7778 | 157016.6667 | 179247.2222 | 164938.8889 | 170886.1111 | 177422.2222 | 161797.2222
BLD4NEW |  |  | Pumps | 284602.7778 | 257344.4444 | 253655.5556 | 210575 | 163933.3333 | 173875 | 121852.7778 | 208127.7778 | 122758.3333 | 87213.8889 | 124130.5556 | 98425 | 116216.6667 | 79005.5556 | 81827.7778 | 45661.1111
BLD4NEW |  |  | Heat Rejection | 223216.6667 | 197050 | 205097.2222 | 158536.1111 | 135213.8889 | 140066.6667 | 100983.3333 | 144263.8889 | 90088.8889 | 68344.4444 | 90111.1111 | 69991.6667 | 84516.6667 | 54886.1111 | 54375 | 30486.1111
BLD4NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Total End Uses | 8076530.5556 | 7490513.8889 | 7346788.8889 | 6783538.8889 | 6346611.1111 | 6372205.5556 | 5741108.3333 | 6580661.1111 | 5841563.8889 | 5496130.5556 | 5944877.7778 | 5598452.7778 | 5855580.5556 | 5402869.4444 | 5439402.7778 | 5127744.4444
BLD4NEW |  |  | Gas (MJ)
BLD4NEW |  |  | Heating | 126210 | 1676210 | 1134140 | 1630540 | 247200 | 726680 | 2210810 | 3247070 | 1563320 | 3019420 | 5002210 | 2850370 | 7573840 | 5267580 | 9235090 | 16667630
BLD4NEW |  |  | Water Systems | 129200 | 163080 | 143490 | 195800 | 189540 | 167010 | 217540 | 221530 | 216640 | 234970 | 244120 | 242950 | 263660 | 267210 | 295860 | 334770
BLD4NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Total End Uses | 255410 | 1839290 | 1277630 | 1826340 | 436740 | 893690 | 2428350 | 3468600 | 1779960 | 3254380 | 5246340 | 3093320 | 7837500 | 5534790 | 9530950 | 17002400
BLD4NEW |  |  | Total Building (MJ) | 29330920 | 28805140 | 27726070 | 26247080 | 23284540 | 23833630 | 23096330 | 27158980 | 22809590 | 23040450 | 26647890 | 23247750 | 28917590 | 24985120 | 29112790 | 35462290
BLD4NEW |  | Energy - End Use Intensities
BLD4NEW |  |  | Electricity (MJ/m2)
BLD4NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Cooling (elec) | 212.7375 | 172.4416 | 157.8061 | 125.6402 | 98.1952 | 95.7002 | 56.4447 | 110.9455 | 61.4352 | 42.9517 | 72.2 | 47.1199 | 65.7052 | 35.2575 | 37.419 | 19.1855
BLD4NEW |  |  | Interior Lighting (elec) | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814
BLD4NEW |  |  | Exterior Lighting (elec) | 17.4144 | 17.4077 | 17.4044 | 17.4016 | 17.3885 | 17.3844 | 17.3936 | 17.3831 | 17.3898 | 17.3552 | 17.3859 | 17.3757 | 17.3744 | 17.3705 | 17.3606 | 17.2544
BLD4NEW |  |  | Interior Equipment (elec) | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998 | 180.9998
BLD4NEW |  |  | Exterior Equipment (elec) | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124
BLD4NEW |  |  | Fans (elec) | 14.4917 | 13.4012 | 16.5314 | 11.8911 | 10.8289 | 14.1676 | 11.4457 | 12.1363 | 15.0431 | 11.1666 | 12.2033 | 13.931 | 12.819 | 13.2812 | 13.7892 | 12.5748
BLD4NEW |  |  | Pumps (elec) | 22.1192 | 20.0007 | 19.714 | 16.3658 | 12.7408 | 13.5135 | 9.4703 | 16.1756 | 9.5407 | 6.7782 | 9.6474 | 7.6495 | 9.0323 | 6.1403 | 6.3596 | 3.5488
BLD4NEW |  |  | Heat Rejection (elec) | 17.3483 | 15.3146 | 15.9401 | 12.3214 | 10.5088 | 10.8859 | 7.8484 | 11.2121 | 7.0017 | 5.3117 | 7.0034 | 5.4397 | 6.5686 | 4.2657 | 4.226 | 2.3694
BLD4NEW |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Total End Uses | 627.7045 | 582.1595 | 570.9893 | 527.2137 | 493.2559 | 495.2451 | 446.1965 | 511.4461 | 454.0038 | 427.1569 | 462.0333 | 435.1093 | 455.0932 | 419.9087 | 422.748 | 398.5261
BLD4NEW |  |  | Gas (MJ/m2)
BLD4NEW |  |  | Heating (gas) | 2.7247 | 36.1873 | 24.4847 | 35.2014 | 5.3367 | 15.6881 | 47.7287 | 70.1002 | 33.7502 | 65.1856 | 107.9916 | 61.536 | 163.5099 | 113.7206 | 199.3742 | 359.8336
BLD4NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Water Systems (gas) | 2.7893 | 3.5207 | 3.0978 | 4.2271 | 4.0919 | 3.6055 | 4.6964 | 4.7826 | 4.677 | 5.0727 | 5.2703 | 5.245 | 5.6921 | 5.7687 | 6.3873 | 7.2273
BLD4NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Total End Uses | 5.514 | 39.708 | 27.5825 | 39.4284 | 9.4287 | 19.2937 | 52.4251 | 74.8828 | 38.4271 | 70.2581 | 113.262 | 66.781 | 169.202 | 119.4893 | 205.7615 | 367.0609
BLD4NEW |  |  | Total Building (MJ/m2) | 633.2185 | 621.8675 | 598.5717 | 566.6422 | 502.6846 | 514.5387 | 498.6213 | 586.329 | 492.431 | 497.415 | 575.2952 | 501.8903 | 624.2952 | 539.398 | 628.5093 | 765.5872
BLD4NEW |  | Peak Energy Demand
BLD4NEW |  |  | Electricity Peak Demand (kW)
BLD4NEW |  |  | Jan | 1682.0876 | 1653.7837 | 1468.7049 | 1498.3553 | 1411.3738 | 1384.0595 | 1315.5876 | 1451.6933 | 1291.5727 | 1095.1557 | 1063.9586 | 1278.3777 | 1064.9826 | 1106.3181 | 1067.0835 | 1115.7112
BLD4NEW |  |  | Feb | 1685.4591 | 1615.8326 | 1510.0413 | 1517.5206 | 1410.251 | 1367.3658 | 1438.3588 | 1395.5117 | 1330.3447 | 1324.5675 | 1063.1928 | 1211.8893 | 1051.5836 | 1286.1972 | 1055.2546 | 1104.3854
BLD4NEW |  |  | Mar | 1680.0878 | 1651.9566 | 1536.2726 | 1559.3358 | 1411.5467 | 1421.1599 | 1363.9482 | 1592.4937 | 1340.4721 | 1368.861 | 1454.0518 | 1330.2471 | 1392.3169 | 1334.8865 | 1054.7604 | 1102.5672
BLD4NEW |  |  | Apr | 1673.7592 | 1647.7654 | 1549.6298 | 1582.5802 | 1454.3389 | 1434.8064 | 1404.135 | 1580.0993 | 1372.8865 | 1355.8215 | 1540.9472 | 1395.5672 | 1462.3119 | 1303.4891 | 1361.1045 | 1049.3536
BLD4NEW |  |  | May | 1678.0008 | 1647.3812 | 1578.5348 | 1609.2306 | 1487.5633 | 1485.239 | 1453.6699 | 1622.1006 | 1396.0227 | 1439.1407 | 1579.877 | 1397.7025 | 1584.4362 | 1370.3829 | 1466.384 | 1315.0379
BLD4NEW |  |  | Jun | 1687.6177 | 1626.9266 | 1616.9177 | 1605.9024 | 1484.3124 | 1492.6788 | 1453.2566 | 1616.7483 | 1707.0344 | 1440.9953 | 1599.0534 | 1455.5197 | 1593.161 | 1434.2532 | 1549.8766 | 1406.7117
BLD4NEW |  |  | Jul | 1660.7863 | 1664.0183 | 1622.7995 | 1593.9533 | 1498.4554 | 1505.9138 | 1479.6132 | 1619.9823 | 1696.2948 | 1481.4016 | 1595.5097 | 1456.0686 | 1597.9551 | 1423.8875 | 1553.5599 | 1395.6076
BLD4NEW |  |  | Aug | 1671.0391 | 1647.5287 | 1637.0468 | 1606.3733 | 1495.8772 | 1505.6497 | 1461.5264 | 1650.5859 | 1464.7291 | 1461.6757 | 1624.0086 | 1458.2539 | 1599.4424 | 1414.5329 | 1551.865 | 1375.7365
BLD4NEW |  |  | Sep | 1650.7022 | 1647.1937 | 1635.9502 | 1607.2302 | 1490.536 | 1499.3475 | 1461.3257 | 1621.3234 | 1444.496 | 1446.3264 | 1610.12 | 1403.189 | 1605.733 | 1417.342 | 1513.243 | 1295.357
BLD4NEW |  |  | Oct | 1670.2637 | 1651.8522 | 1606.213 | 1598.3531 | 1492.8876 | 1453.997 | 1453.0582 | 1625.9328 | 1433.2923 | 1400.5754 | 1602.7798 | 1368.492 | 1498.9106 | 1368.1202 | 1397.9467 | 1100.7354
BLD4NEW |  |  | Nov | 1677.9358 | 1652.0943 | 1543.836 | 1517.2813 | 1499.1693 | 1435.763 | 1454.0607 | 1575.6546 | 1336.419 | 1389.3843 | 1606.4653 | 1285.6736 | 1431.8869 | 1161.1644 | 1129.7155 | 1101.9956
BLD4NEW |  |  | Dec | 1677.1618 | 1655.7223 | 1516.9842 | 1520.0391 | 1450.4964 | 1398.8485 | 1300.1231 | 1288.8541 | 1226.4463 | 1095.1379 | 1102.4765 | 1177.3301 | 1064.0692 | 1105.0578 | 1066.2667 | 1103.4661
BLD4NEW |  |  | Time of Peak Electrical Demand
BLD4NEW |  |  | Jan | 05-JAN-08:09 | 20-JAN-08:09 | 26-JAN-16:10 | 24-JAN-16:00 | 25-JAN-16:10 | 18-JAN-16:49 | 06-JAN-16:10 | 09-JAN-08:00 | 26-JAN-16:40 | 04-JAN-16:00 | 27-JAN-16:00 | 27-JAN-16:10 | 04-JAN-16:00 | 17-JAN-08:09 | 09-JAN-16:40 | 02-JAN-08:09
BLD4NEW |  |  | Feb | 03-FEB-08:09 | 21-FEB-08:09 | 28-FEB-16:10 | 22-FEB-08:09 | 13-FEB-16:10 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:30 | 21-FEB-16:10 | 01-FEB-16:00 | 07-FEB-15:09 | 07-FEB-08:09 | 02-FEB-16:40 | 01-FEB-08:09 | 03-FEB-08:09
BLD4NEW |  |  | Mar | 07-MAR-08:09 | 08-MAR-08:09 | 22-MAR-15:00 | 29-MAR-15:39 | 31-MAR-15:09 | 31-MAR-15:00 | 30-MAR-15:39 | 09-MAR-16:19 | 02-MAR-16:10 | 29-MAR-15:00 | 31-MAR-15:39 | 30-MAR-15:00 | 23-MAR-15:00 | 30-MAR-15:00 | 22-MAR-15:09 | 14-MAR-07:10
BLD4NEW |  |  | Apr | 17-APR-07:10 | 17-APR-07:00 | 03-APR-15:09 | 13-APR-07:00 | 11-APR-15:09 | 10-APR-15:09 | 13-APR-15:09 | 04-APR-15:00 | 20-APR-15:00 | 19-APR-15:00 | 10-APR-07:00 | 25-APR-15:50 | 27-APR-15:09 | 06-APR-15:00 | 04-APR-15:00 | 10-APR-07:10
BLD4NEW |  |  | May | 26-MAY-07:10 | 05-MAY-07:10 | 22-MAY-07:00 | 23-MAY-07:10 | 31-MAY-07:10 | 19-MAY-07:00 | 25-MAY-15:00 | 15-MAY-07:10 | 26-MAY-15:39 | 31-MAY-15:00 | 25-MAY-15:20 | 24-MAY-15:09 | 31-MAY-07:40 | 26-MAY-15:09 | 31-MAY-15:00 | 30-MAY-15:09
BLD4NEW |  |  | Jun | 27-JUN-15:50 | 05-JUN-07:10 | 13-JUN-07:40 | 06-JUN-07:10 | 29-JUN-07:19 | 13-JUN-07:10 | 26-JUN-15:00 | 27-JUN-07:10 | 29-JUN-15:00 | 29-JUN-15:09 | 14-JUN-07:10 | 27-JUN-15:20 | 21-JUN-07:10 | 23-JUN-07:00 | 15-JUN-07:00 | 22-JUN-15:30
BLD4NEW |  |  | Jul | 13-JUL-15:39 | 18-JUL-15:00 | 11-JUL-15:00 | 18-JUL-07:10 | 31-JUL-07:00 | 28-JUL-07:10 | 03-JUL-07:40 | 25-JUL-15:39 | 07-JUL-15:00 | 31-JUL-07:00 | 25-JUL-07:10 | 25-JUL-07:10 | 17-JUL-07:10 | 21-JUL-15:00 | 11-JUL-07:19 | 24-JUL-15:00
BLD4NEW |  |  | Aug | 21-AUG-15:09 | 31-AUG-15:00 | 28-AUG-07:19 | 09-AUG-07:10 | 18-AUG-07:49 | 14-AUG-07:10 | 09-AUG-15:39 | 09-AUG-15:09 | 17-AUG-07:30 | 21-AUG-15:00 | 04-AUG-15:50 | 11-AUG-15:50 | 31-AUG-07:10 | 15-AUG-15:20 | 17-AUG-07:10 | 18-AUG-15:00
BLD4NEW |  |  | Sep | 29-SEP-07:10 | 15-SEP-15:20 | 18-SEP-07:10 | 25-SEP-07:10 | 11-SEP-07:40 | 05-SEP-07:30 | 22-SEP-15:50 | 27-SEP-07:10 | 07-SEP-07:00 | 29-SEP-15:00 | 08-SEP-07:10 | 12-SEP-15:00 | 22-SEP-07:19 | 13-SEP-15:00 | 06-SEP-15:00 | 01-SEP-15:00
BLD4NEW |  |  | Oct | 31-OCT-07:10 | 23-OCT-07:10 | 04-OCT-07:00 | 20-OCT-07:00 | 23-OCT-07:00 | 06-OCT-15:00 | 31-OCT-15:09 | 03-OCT-07:10 | 03-OCT-15:50 | 17-OCT-15:09 | 31-OCT-07:00 | 04-OCT-15:00 | 06-OCT-15:20 | 05-OCT-15:00 | 27-OCT-15:09 | 30-OCT-07:10
BLD4NEW |  |  | Nov | 15-NOV-08:09 | 20-NOV-08:09 | 06-NOV-16:49 | 22-NOV-16:10 | 09-NOV-16:00 | 10-NOV-16:40 | 16-NOV-16:00 | 03-NOV-15:00 | 08-NOV-16:10 | 03-NOV-15:09 | 02-NOV-07:00 | 10-NOV-16:10 | 02-NOV-15:30 | 21-NOV-13:00 | 09-NOV-16:40 | 06-NOV-08:09
BLD4NEW |  |  | Dec | 18-DEC-08:09 | 20-DEC-08:09 | 13-DEC-16:10 | 26-DEC-08:00 | 29-DEC-16:00 | 05-DEC-16:30 | 07-DEC-15:30 | 08-DEC-09:00 | 08-DEC-15:09 | 01-DEC-16:00 | 27-DEC-16:00 | 21-DEC-16:10 | 29-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 29-DEC-08:09
BLD4NEW |  | Source Energy
BLD4NEW |  |  | Total Source Energy (GJ) | 96722.39 | 99948.48 | 85051.59 | 84145.72 | 71190.87 | 83032.07 | 66619.17 | 88504.52 | 71720.04 | 38021.12 | 81618.92 | 70250.31 | 81010.8 | 73653.34 | 77710.6 | 84505.33
BLD4NEW |  |  | Total Source Energy (MJ/m2) | 2088.12 | 2157.76 | 1836.16 | 1816.6 | 1536.92 | 1792.56 | 1438.23 | 1910.7 | 1548.35 | 820.83 | 1762.05 | 1516.62 | 1748.92 | 1590.09 | 1677.68 | 1824.37
BLD4NEW |  | Water Consumption (m3)
BLD4NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Heat Rejection | 23558.49 | 19025.68 | 28145.38 | 13877.54 | 9866.62 | 20187.07 | 5820.69 | 12374.13 | 11408.24 | 4618.08 | 8430.8 | 8374.75 | 7553.58 | 5794.98 | 4275.73 | 2377.49
BLD4NEW |  |  | Water Systems | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13
BLD4NEW |  |  | Total Building | 25062.63 | 20529.81 | 29649.52 | 15381.67 | 11370.76 | 21691.2 | 7324.82 | 13878.26 | 12912.37 | 6122.21 | 9934.93 | 9878.89 | 9057.71 | 7299.12 | 5779.87 | 3881.62
BLD4NEW |  | Emissions
BLD4NEW |  |  | Carbon Equivalent (kg) | 2219590 | 2531710 | 2240850 | 2122510 | 749577.4991 | 2165300 | 714728.7878 | 1838380 | 2418360 | 458991.0929 | 3264110 | 2342740 | 2145660 | 2074220 | 2033740 | 1749480
BLD4NEW |  |  | CO2 (kg) | 5142230 | 6365390 | 5282200 | 4837660 | 2002970 | 5136930 | 1917810 | 4163070 | 5652970 | 1120470 | 7586250 | 5489990 | 5029090 | 4880590 | 4788900 | 4500270
BLD4NEW |  |  | NOX (kg) | 9057.4732 | 8327.7631 | 8875.6979 | 9244.1617 | 1715.2793 | 8390.1156 | 1647.8053 | 8126.4022 | 9839.8388 | 1681.8127 | 13564.1996 | 9495.9548 | 8802.7479 | 8413.4294 | 8283.5519 | 5332.4231
BLD4NEW |  |  | SO2 (kg) | 34570.8539 | 35730.2481 | 29543.2535 | 23810.7067 | 18467.9961 | 35052.4681 | 16706.5836 | 24022.9771 | 25509.4221 | 4248.942 | 40065.1179 | 24448.1549 | 13822.2043 | 14427.7943 | 12840.412 | 26106.8319
BLD4NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD4NEW |  |  | Hg (kg) | 0.1575 | 0.1006 | 0.0802 | 0.087 | 0.0083 | 0.0657 | 0.0077 | 0.0971 | 0.0995 | 0.0168 | 0.1213 | 0.0955 | 0.1016 | 0.1006 | 0.0946 | 0.0901
BLD4NEW |  |  | Water for Electricity (m3) | 4278.61 | 12187.9 | 218232 | 42353.7 | 111432 | 174815 | 100801 | 1494.06 | 26525.4 | 56152.9 | 9223.12 | 25421.5 | 9084.58 | 342240 | 8438.91 | 5238.91

## Picture
DOE Commercial Building Benchmark - Large Office

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
|  | INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
[5 empty] | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
[5 empty] | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
|  | BLDG_OCC_SCH | Fraction | Through 12/31 | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1 | 54.5 | 2841.79
SchOcc | WD |  |  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | 10.2
| Sat |  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchLight | WD | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 11.3 | 60.8 | 3170.29
| Sat |  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4.3
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
SchElec | WD | BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 15 | 83.75 | 4366.96
| Sat |  |  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.75
[5 empty] | SummerDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SetCool | WD | CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
| Sat |  |  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
[5 empty] | WinterDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
| Sun |  |  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
SetHeat | WD | HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
[5 empty] | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
| Sat |  |  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
[5 empty] | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
| Sun |  |  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
|  | MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
[5 empty] | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
[5 empty] | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
|  | HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
SchGas | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 29.42 | 1534.04
| Sat |  |  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
| Sun |  |  |  | Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
|  | Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600