## 1
1 | Building Summary Secondary School pre-1980 construction
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 19592 | 19592 | 19592
nFloor |  | Number of Floors | 2 | 2 | 2
glazing |  | Total | 0.5 | 0.5 | 0.5
hCeiling |  | Floor to Ceiling Height (m) | 4.5 | 4.5 | 4.5
areaWall |  | Gross Dimensions - Total Area (m2) | 6384 | 6384 | 6384
ver2hor |  | Wall to Skin Ratio | 0.35 | 0.35 | 0.35
areaRoof |  | Gross Dimensions - Total Area (m2) | 11902 | 11902 | 11902
areaWindow |  | Total Area (m2) | 2089.17 | 2089.17 | 2089.17

## 2
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD10PRE | Total | Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 811.7775 | 9.9 | 14.9508 | 12.3418 | 1615.6901 | 10 | 2.84 | 55583.0362 |  | 0.61445
BLD10PST | Total | Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 811.7775 | 9.9 | 14.9508 | 12.3418 | 1615.6901 | 10 | 2.84 | 55583.0362 |  | 0.61445
BLD10NEW | Total | Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 811.7775 | 9.9 | 14.9508 | 12.3418 | 1615.6901 | 10 | 2.84 | 55583.0362 |  | 0.61445
24.1347

## 3
3 |  | Location Summary
Building | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD10PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD10PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD10PRE | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD10PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD10PRE | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD10PRE | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD10PRE | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD10PRE | HVAC |  | Air Conditioning (kW) | 2508.2872 | 2586.8159 | 2658.0779 | 2587.0625 | 2080.6488 | 2385.7546 | 1986.2685 | 2476.0274 | 1843.2445 | 1801.6323 | 2087.7959 | 1584.2991 | 2001.4703 | 1394.5393 | 1900.4452 | 1484.3949
BLD10PRE | HEAT |  | Heating (kW) | 2274.1572 | 2965.0393 | 2586.7712 | 3207.3233 | 2291.8832 | 2726.6743 | 2675.9722 | 3499.5521 | 2759.9246 | 2984.1803 | 3927.9908 | 3174.7513 | 4238.4278 | 3871.497 | 4331.2903 | 5476.7705
BLD10PRE | COP |  | Air Conditioning (COP) | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081
BLD10PRE | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 104.57 | 108 | 115.33 | 109.89 | 99.63 | 112.45 | 118.31 | 103.88 | 101.53 | 99.83 | 86.71 | 83.33 | 83.35 | 82.47 | 80.83 | 92.16
BLD10PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD10PST | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD10PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD10PST | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD10PST | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD10PST | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD10PST | HVAC |  | Air Conditioning (kW) | 2737.6387 | 2516.7278 | 2298.9302 | 2331.4039 | 2089.1321 | 1962.1853 | 1789.8304 | 2268.0383 | 1516.1452 | 1556.6179 | 2247.5348 | 1462.067 | 2126.4841 | 1273.6199 | 1908.3818 | 1286.6883
BLD10PST | HEAT |  | Heating (kW) | 2353.5783 | 2780.2315 | 2429.2666 | 2953.7438 | 2348.8006 | 2497.6382 | 2727.5954 | 3131.6899 | 2518.2427 | 2767.3755 | 3621.3014 | 2887.0059 | 3827.022 | 3507.8012 | 3909.3425 | 5119.3991
BLD10PST | COP |  | Air Conditioning (COP) | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081
BLD10PST | EffHeat |  | Heating Efficiency (%) | 0.75056 | 0.75449 | 0.75304 | 0.75522 | 0.75158 | 0.75471 | 0.74941 | 0.7574 | 0.75669 | 0.75597 | 0.75798 | 0.75897 | 0.75927 | 0.75895 | 0.75927 | 0.75637
BLD10PST | Fan |  | Fan Max Flow Rate (m3/s ) | 99.42 | 86.6 | 90.06 | 85.45 | 94.3 | 84.54 | 102.97 | 79.08 | 80.14 | 81.24 | 78.3 | 75.07 | 75.15 | 76.03 | 75.18 | 83.63
BLD10NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD10NEW | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD10NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD10NEW | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD10NEW | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD10NEW | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD10NEW | HVAC |  | Air Conditioning (kW) | 2366.4351 | 2376.4979 | 2198.1583 | 2186.7101 | 1739.3277 | 1875.8505 | 1706.96 | 2254.945 | 1536.8229 | 1510.2075 | 2217.7102 | 1499.5154 | 2136.6229 | 1286.0534 | 1926.1349 | 1058.063
BLD10NEW | HEAT |  | Heating (kW) | 2044.9665 | 2673.103 | 2332.4303 | 2804.2449 | 1999.2278 | 2390.7851 | 2648.024 | 3145.4754 | 2513.1179 | 2681.3805 | 3598.1434 | 2905.4783 | 3857.8248 | 3487.6808 | 3950.8641 | 4572.8564
BLD10NEW | COP |  | Air Conditioning (COP) | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081
BLD10NEW | EffHeat |  | Heating Efficiency (%) | 0.7713 | 0.78022 | 0.77083 | 0.78022 | 0.77227 | 0.77168 | 0.78035 | 0.78022 | 0.77176 | 0.78018 | 0.78022 | 0.78021 | 0.78022 | 0.78021 | 0.78021 | 0.78021
BLD10NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 79.44 | 80.99 | 84.3 | 78.14 | 72.39 | 78.41 | 97.67 | 79.78 | 80.17 | 76.97 | 78.04 | 76.76 | 77.28 | 75.81 | 77.58 | 68.32
2.52

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip1 | WD | BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69 | 3348.11
| Sat |  |  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
| Sun |  |  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
SchLight1 | WD | BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87 | 3466.2
| Sat |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
| Sun |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
SchOcc1 | WD | BLDG_OCC_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75 | 1457.54
| Sat |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool1 | WD | CLGSETP_SCH | Temperature | Through 6/30 | Other | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 576 | 1296 | 67577.14
| Sat |  |  |  | WE, Hol, WinterDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 648
| Sun |  |  |  | WE, Hol, WinterDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371
SetHeat1 | WD | HTGSETP_SCH | Temperature | Through 6/30 | Other | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 504 | 768 | 40045.71
| Sat |  |  |  | WE, Hol, SummerDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 384
| Sun |  |  |  | WE, Hol, SummerDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 384
SchGas1 | WD | KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 7.2 | 389.41
| Sat |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
| Sun |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
SchSWH1 | WD | BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09
| Sat |  |  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
| Sun |  |  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
SchEquip2 | WD | BLDG_EQUIP_SCH | Fraction | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 41.25
| Sat |  |  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
| Sun |  |  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
SchLight2 | WD | BLDG_LIGHT_SCH | Fraction | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 40.64
| Sat |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
| Sun |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
SchOcc2 | WD | BLDG_OCC_SCH | Fraction | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
| Sat |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool2 | WD | KITCHEN_GAS_EQUIP_SCH | Fraction | Through 9/1 | SummerDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 576 | 1296
| Sat |  |  |  | WE, Hol, WinterDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 648
| Sun |  |  |  | WE, Hol, WinterDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 648
SetHeat2 | WD | CLGSETP_SCH | Temperature | Through 9/1 | WinterDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 504 | 768
| Sat |  |  |  | WE, Hol, SummerDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 384
| Sun |  |  |  | WE, Hol, SummerDesign | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 384
SchGas2 | WD | HTGSETP_SCH | Temperature | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.19 | 6.91
| Sat |  |  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
| Sun |  |  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
SchSWH2 | WD |  |  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54
| Sat |  |  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
| Sun |  |  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84

## BuildingSummary
1 | Building Summary Secondary School pre-1980 construction
UWG |  |  | Value | Value | Value
Program
|  | Building Name | Secondary School Reference Building new construction 90.1-2004 | Secondary School Reference Building new construction 90.1-2004 | Secondary School Reference Building new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Education | Education | Education
Form
areaFloor |  | Total Floor Area (m2) | 19592 | 19592 | 19592
|  | Building Shape | "E" Shape | "E" Shape | "E" Shape
Aspect Ratio
nFloor |  | Number of Floors | 2 | 2 | 2
Window Fraction (Window to Wall Ratio)
|  | South | 0.35 | 0.35 | 0.35
|  | East | 0.35 | 0.35 | 0.35
|  | North | 0.35 | 0.35 | 0.35
|  | West | 0.28 | 0.28 | 0.28
glazing |  | Total | 0.34 | 0.34 | 0.34
|  | Skylight/TDD Percentage |  |  | 1.12%
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | See pictures | See pictures | See pictures
hCeiling |  | Floor to Ceiling Height (m) | 4 | 4 | 4
|  | Roof type | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Steel-Framed | Steel-Framed | Steel-Framed
areaWall |  | Gross Dimensions - Total Area (m2) | 6384 | 6384 | 6384
|  | Net Dimensions - Total Area (m2) | 4088.16 | 4088.16 | 4088.16
ver2hor |  | Wall to Skin Ratio | 0.35 | 0.35 | 0.35
Roof
|  | Construction Type | IEAD | IEAD | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 11902 | 11902 | 11902
|  | Net Dimensions - Total Area (m2) | 11768.6976 | 11768.6976 | 11768.6976
|  | Roof to Skin Ratio | 0.65 | 0.65 | 0.65
Window Dimensions (m2)
|  | South | 753.18 | 753.18 | 753.18
|  | East | 291.61 | 291.61 | 291.61
|  | North | 753.18 | 753.18 | 753.18
|  | West | 291.2 | 291.2 | 291.2
areaWindow |  | Total Area (m2) | 2089.17 | 2089.17 | 2089.17
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) |  |  | 133.8
|  | Operable area (m2) |  |  | 0
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
|  | Dimensions - Total Area (m2) | 11902 | 11902 | 11902
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 6792 | 6792 | 6792
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 39184 | 39184 | 39184
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 0.60327 | 0.60327 | 0.16087
HVAC
|  | System Type | MZ CAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria) | MZ VAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria) | MZ VAV, PSZ-AC (gym, aux gym, auditorium, kitchen, & cafeteria)
|  | Heating Type | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria) | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria) | Boiler, gas heat (gym, aux gym, auditorium, kitchen, & cafeteria)
|  | Cooling Type | Packaged DX | Air cooled chiller, PACU (gym, aux gym, auditorium, kitchen, & cafeteria) | Air cooled chiller, PACU (gym, aux gym, auditorium, kitchen, & cafeteria)
|  | Fan Control | Constant | Variable, constant (gym, aux gym, auditorium, kitchen, & cafeteria) | Variable, constant (gym, aux gym, auditorium, kitchen, & cafeteria)
Service Water Heating
|  | SWH Type | Storage Tank | Storage Tank | Storage Tank
|  | Fuel | Natural Gas | Natural Gas | Natural Gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 2677.93 | 2677.93 | 2677.93

## ZoneSummary
2 |  | Zone Summary
BLD | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 10.745 | 4 |  |  |  | 0.5 | 570 |  | 0.17901
|  | LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 12.0086 | 4 |  |  |  | 0.5 | 105 |  | 0.29153
|  | BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6069 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.56362
|  | OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 20.0991 | 10.7639 |  |  | 10 |  | 266 |  | 0.39893
|  | GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.2801 | 1 | 1976 | 11.3864 | 5 |  | 717.2337 | 10 |  | 19760 |  | 0
|  | AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608.0006 | 266.3502 | 3 | 416 | 11.8138 | 5 |  |  | 10 |  | 4160 |  | 0.24855
|  | AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512.0005 | 106.4001 | 1 | 988 | 12.0812 | 5 |  |  | 8 |  | 7904 |  | 0.26438
|  | KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6 | 36 | 16.7657 | 222.2745 | 1119.4456 | 503.4582 | 8 |  | 288 | 1887.788 | 0.17006
|  | CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200.0002 | 70.0001 | 1.39 | 448.9209 | 14.3812 | 19.2674 |  |  | 10 |  | 4489.2086 |  | 0.32703
|  | MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 8.0563 | 4 |  |  |  | 0.25 | 85.5 |  | 0
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 20 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 20 |  |  | 8 |  | 954 |  | 1.4738
|  | MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 10.745 | 4 |  |  |  | 0.5 | 570 |  | 1.1994
|  | LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 12.0086 | 4 |  |  |  | 0.5 | 105 |  | 1.3119
|  | BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6069 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 1.584
|  | OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 20.0991 | 10.7639 |  |  | 10 |  | 266 |  | 1.4193
|  | LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236.0002 | 83.0101 | 4.35 | 193.1034 | 16.3387 | 10 |  |  | 8 |  | 1544.8276 |  | 1.307
|  | MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 8.0563 | 4 |  |  |  | 0.25 | 85.5 |  | 1.0203
BLD10PRE | Total | Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 6080.0643 | 15.4421 | 10.336 | 12.3418 | 1615.6901 |  | 2.837 | 55583.0362 |  | 0.7038
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 0.063771
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 0.82452
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 0.45349
|  | MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 10.745 | 4 |  |  |  | 0.5 | 570 |  | 0.17901
|  | LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 12.0086 | 4 |  |  |  | 0.5 | 105 |  | 0.29153
|  | BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6069 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.56362
|  | OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 20.0991 | 10.7639 |  |  | 10 |  | 266 |  | 0.39893
|  | GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.2801 | 1 | 1976 | 11.3864 | 5 |  | 717.2337 | 10 |  | 19760 |  | 0
|  | AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608.0006 | 266.3502 | 3 | 416 | 11.8138 | 5 |  |  | 10 |  | 4160 |  | 0.24855
|  | AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512.0005 | 106.4001 | 1 | 988 | 12.0812 | 5 |  |  | 8 |  | 7904 |  | 0.26438
|  | KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6 | 36 | 16.7657 | 222.2745 | 1119.4456 | 503.4582 | 8 |  | 288 | 1887.788 | 0.17006
|  | CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200.0002 | 70.0001 | 1.39 | 448.9209 | 14.3812 | 19.2674 |  |  | 10 |  | 4489.2086 |  | 0.32703
|  | MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 8.0563 | 4 |  |  |  | 0.25 | 85.5 |  | 0
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 10 |  |  | 8 |  | 954 |  | 1.4738
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 20 |  |  | 8 |  | 954 |  | 1.4738
|  | CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 9.255 | 4 |  |  |  | 0.5 | 160 |  | 1.0841
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 21.5278 | 10 |  |  | 8 |  | 198 |  | 1.8449
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 21.5278 | 20 |  |  | 8 |  | 954 |  | 1.4738
|  | MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 10.745 | 4 |  |  |  | 0.5 | 570 |  | 1.1994
|  | LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 12.0086 | 4 |  |  |  | 0.5 | 105 |  | 1.3119
|  | BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6069 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 1.584
|  | OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 20.0991 | 10.7639 |  |  | 10 |  | 266 |  | 1.4193
|  | LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236.0002 | 83.0101 | 4.35 | 193.1034 | 16.3387 | 10 |  |  | 8 |  | 1544.8276 |  | 1.307
|  | MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 8.0563 | 4 |  |  |  | 0.25 | 85.5 |  | 1.0203
BLD10PST | Total | Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 6080.0643 | 15.4421 | 10.336 | 12.3418 | 1615.6901 |  | 2.837 | 55583.0362 |  | 0.7038
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
|  | CORRIDOR_POD_1_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
|  | CORRIDOR_POD_2_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
|  | CORRIDOR_POD_3_ZN_1_FLR_1 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.017006
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.21987
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.12093
|  | MAIN_CORRIDOR_ZN_1_FLR_1 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 5.3819 | 4 |  |  |  | 0.5 | 570 |  | 0.047735
|  | LOBBY_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 13.9931 | 4 |  |  |  | 0.5 | 105 |  | 0.07774
|  | BATHROOMS_ZN_1_FLR_1 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6875 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.1503
|  | OFFICES_ZN_1_FLR_1 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 11.8403 | 10.7639 |  |  | 10 |  | 266 |  | 0.10638
|  | GYM_ZN_1_FLR_1 | Yes | 1 | 1976 | 15808 | 8 | 0 | 80.2801 | 1 | 1976 | 15.0695 | 5 |  | 717.2337 | 10 |  | 19760 |  | 0
|  | AUX_GYM_ZN_1_FLR_1 | Yes | 1 | 1248 | 9984 | 8 | 608.0006 | 266.3502 | 3 | 416 | 15.0695 | 5 |  |  | 10 |  | 4160 |  | 0.066279
|  | AUDITORIUM_ZN_1_FLR_1 | Yes | 1 | 988 | 7904 | 8 | 512.0005 | 106.4001 | 1 | 988 | 9.6875 | 5 |  |  | 8 |  | 7904 |  | 0.070501
|  | KITCHEN_ZN_1_FLR_1 | Yes | 1 | 216 | 864 | 4 | 36 | 12.6 | 6 | 36 | 12.9167 | 222.2745 | 1119.4456 | 503.4582 | 8 |  | 288 | 1887.788 | 0.045349
|  | CAFETERIA_ZN_1_FLR_1 | Yes | 1 | 624 | 2496 | 4 | 200.0002 | 70.0001 | 1.39 | 448.9209 | 15.0695 | 19.2674 |  |  | 10 |  | 4489.2086 |  | 0.087209
|  | MECH_ZN_1_FLR_1 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.1458 | 4 |  |  |  | 0.25 | 85.5 |  | 0
|  | CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_1_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
|  | CORRIDOR_POD_1_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
|  | CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_2_POD_1_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
|  | CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_1_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
|  | CORRIDOR_POD_2_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
|  | CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_2_POD_2_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 10 |  |  | 8 |  | 954 |  | 0.39302
|  | CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_1_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 20 |  |  | 8 |  | 954 |  | 0.39302
|  | CORRIDOR_POD_3_ZN_1_FLR_2 | Yes | 1 | 320 | 1280 | 4 | 20 | 7 | 10 | 32 | 5.3819 | 4 |  |  |  | 0.5 | 160 |  | 0.2891
|  | CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 99 | 396 | 4 | 80.0001 | 28 | 4 | 24.75 | 15.0695 | 10 |  |  | 8 |  | 198 |  | 0.49196
|  | MULT_CLASS_2_POD_3_ZN_1_FLR_2 | Yes | 1 | 477 | 1908 | 4 | 212.0002 | 74.2001 | 4 | 119.25 | 15.0695 | 20 |  |  | 8 |  | 954 |  | 0.39302
|  | MAIN_CORRIDOR_ZN_1_FLR_2 | Yes | 1 | 1140 | 4560 | 4 | 200.0002 | 70.0001 |  | 0 | 5.3819 | 4 |  |  |  | 0.5 | 570 |  | 0.31983
|  | LOBBY_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 60.0001 | 21 |  | 0 | 13.9931 | 4 |  |  |  | 0.5 | 105 |  | 0.34983
|  | BATHROOMS_ZN_1_FLR_2 | Yes | 1 | 210 | 840 | 4 | 116.0001 | 40.6 | 10 | 21 | 9.6875 | 4 |  | 197.4991 | 25 |  | 300 | 300 | 0.42239
|  | OFFICES_ZN_1_FLR_2 | Yes | 1 | 532 | 2128 | 4 | 208.0002 | 72.8001 | 20 | 26.6 | 11.8403 | 10.7639 |  |  | 10 |  | 266 |  | 0.37847
|  | LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | Yes | 1 | 840 | 3360 | 4 | 236.0002 | 83.0101 | 4.35 | 193.1034 | 13.9931 | 10 |  |  | 8 |  | 1544.8276 |  | 0.34854
|  | MECH_ZN_1_FLR_2 | Yes | 1 | 342 | 1368 | 4 | 0 | 0 | 100 | 3.42 | 16.1458 | 4 |  |  |  | 0.25 | 85.5 |  | 0.27209
BLD10NEW | Total | Total Conditioned Zones |  |  | 19592 | 95216 |  | 6384.0059 | 2295.8421 |  | 6080.0643 | 12.3752 | 10.336 | 12.3418 | 1615.6901 | 10 | 2.837 | 55583.0362 |  | 0.18768

## LocationSummary
3 |  | Location Summary
Building | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD10PRE |  | Program
BLD10PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD10PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD10PRE
BLD10PRE |  | Fabric
BLD10PRE |  |  | Exterior walls
BLD10PRE | TypeWall |  | Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
BLD10PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD10PRE |  |  | Roof
BLD10PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD10PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD10PRE |  |  | Window
BLD10PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD10PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD10PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD10PRE |  |  | Skylights/TDD
BLD10PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD10PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD10PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD10PRE |  |  | Foundation
BLD10PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD10PRE |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD10PRE |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD10PRE |  | HVAC
BLD10PRE |  |  | HVAC Sizing
BLD10PRE | HVAC |  | Air Conditioning (kW) | 2508.2872 | 2586.8159 | 2658.0779 | 2587.0625 | 2080.6488 | 2385.7546 | 1986.2685 | 2476.0274 | 1843.2445 | 1801.6323 | 2087.7959 | 1584.2991 | 2001.4703 | 1394.5393 | 1900.4452 | 1484.3949
BLD10PRE |  |  | PSZ-AC_1:5_COOLC DXCOIL | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 360.1228 | 490.6879 | 441.5488 | 424.2531 | 490.6879 | 431.1614 | 490.6879 | 363.8108 | 490.6879 | 327.0982
BLD10PRE |  |  | PSZ-AC_2:6_COOLC DXCOIL | 174.2979 | 177.0996 | 190.3428 | 183.2504 | 136.4944 | 157.9122 | 96.6414 | 160.5401 | 118.9152 | 104.2647 | 110.1096 | 91.2249 | 103.5975 | 91.4574 | 112.0083 | 95.2948
BLD10PRE |  |  | PSZ-AC_3:7_COOLC DXCOIL | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 160.8007 | 196.2751 | 162.4093 | 157.7322 | 196.2751 | 162.599 | 196.2751 | 130.8393 | 196.2751 | 130.8393
BLD10PRE |  |  | PSZ-AC_4:8_COOLC DXCOIL | 20.0622 | 19.8975 | 19.2452 | 20.4981 | 16.6255 | 16.6792 | 21.6259 | 18.1202 | 14.5438 | 12.0392 | 14.58 | 12.531 | 14.5292 | 10.4426 | 11.6405 | 8.7152
BLD10PRE |  |  | PSZ-AC_5:9_COOLC DXCOIL | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 86.162 | 111.4777 | 92.7716 | 88.9175 | 111.4777 | 102.9694 | 111.4777 | 88.4408 | 111.4777 | 74.3123
BLD10PRE |  |  | CAV_OTHER_COOLC DXCOIL | 481.8773 | 501.7724 | 493.9393 | 473.7112 | 342.2515 | 423.1989 | 353.6084 | 451.5769 | 323.6482 | 292.7036 | 377.2356 | 238.8526 | 341.0345 | 240.4912 | 310.0912 | 285.7798
BLD10PRE |  |  | CAV_POD_1_COOLC DXCOIL | 338.8604 | 357.5669 | 380.5207 | 365.7861 | 258.4506 | 325.1288 | 302.0724 | 343.8556 | 225.052 | 237.1685 | 256.7769 | 177.5911 | 242.2971 | 151.9538 | 221.5184 | 187.3702
BLD10PRE |  |  | CAV_POD_2_COOLC DXCOIL | 338.3936 | 356.9963 | 380.1191 | 365.3426 | 257.8505 | 324.6592 | 301.8259 | 342.7334 | 224.8022 | 236.0979 | 256.7595 | 177.3518 | 242.1854 | 152.3766 | 221.3287 | 187.2474
BLD10PRE |  |  | CAV_POD_3_COOLC DXCOIL | 356.355 | 375.0424 | 395.4701 | 380.0332 | 270.5356 | 339.7355 | 303.4089 | 360.7604 | 239.5535 | 248.4556 | 273.8935 | 190.0179 | 259.386 | 164.7268 | 225.4172 | 187.7379
BLD10PRE | HEAT |  | Heating (kW) | 2274.1572 | 2965.0393 | 2586.7712 | 3207.3233 | 2291.8832 | 2726.6743 | 2675.9722 | 3499.5521 | 2759.9246 | 2984.1803 | 3927.9908 | 3174.7513 | 4238.4278 | 3871.497 | 4331.2903 | 5476.7705
BLD10PRE |  |  | HEATSYS1 BOILER | 777.737 | 1011.6476 | 918.7219 | 1101.9534 | 764.0493 | 955.187 | 967.8995 | 1189.1892 | 936.7857 | 1006.4973 | 1296.4053 | 1047.8757 | 1401.8335 | 1282.9229 | 1430.0657 | 1853.5609
BLD10PRE |  |  | PSZ-AC_1:5_HEATC | 765.0269 | 1009.9404 | 852.0818 | 1089.4655 | 795.6607 | 921.1228 | 879.4681 | 1212.7703 | 963.6127 | 1048.8159 | 1416.7661 | 1150.2765 | 1531.1076 | 1395.2101 | 1567.2052 | 1940.738
BLD10PRE |  |  | PSZ-AC_2:6_HEATC | 220.2998 | 269.0769 | 248.1338 | 287.0945 | 206.1868 | 241.3382 | 212.0087 | 292.1738 | 221.5743 | 239.9511 | 284.1458 | 223.8021 | 299.8608 | 281.1413 | 313.9105 | 413.5578
BLD10PRE |  |  | PSZ-AC_3:7_HEATC | 306.0108 | 403.9762 | 340.8327 | 435.7862 | 318.2643 | 368.4491 | 367.4079 | 485.1081 | 385.4451 | 419.5263 | 566.7064 | 460.1106 | 612.443 | 558.084 | 626.8821 | 776.2952
BLD10PRE |  |  | PSZ-AC_4:8_HEATC | 31.2788 | 40.9532 | 33.4194 | 45.5116 | 26.9586 | 31.3103 | 49.3846 | 44.7855 | 33.5869 | 31.1127 | 42.0968 | 31.3588 | 45.3358 | 37.1655 | 37.1786 | 51.7088
BLD10PRE |  |  | PSZ-AC_5:9_HEATC | 173.8039 | 229.445 | 193.5816 | 247.512 | 180.7635 | 209.2668 | 199.8034 | 275.5253 | 218.92 | 238.277 | 321.8704 | 261.3275 | 347.8472 | 316.9731 | 356.0481 | 440.9098
BLD10PRE |  |  | HVAC Efficiency
BLD10PRE | COP |  | Air Conditioning (COP) | 3.1522 | 3.1516 | 3.1514 | 3.1519 | 3.1557 | 3.1533 | 3.1513 | 3.1529 | 3.1546 | 3.1531 | 3.1538 | 3.1912 | 3.1545 | 3.19 | 3.1787 | 3.1913
BLD10PRE |  |  | PSZ-AC_1:5_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD10PRE |  |  | PSZ-AC_2:6_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD10PRE |  |  | PSZ-AC_3:7_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD10PRE |  |  | PSZ-AC_4:8_COOLC DXCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD10PRE |  |  | PSZ-AC_5:9_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD10PRE |  |  | CAV_OTHER_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD10PRE |  |  | CAV_POD_1_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.13 | 3.23 | 3.23 | 3.23
BLD10PRE |  |  | CAV_POD_2_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.13 | 3.23 | 3.23 | 3.23
BLD10PRE |  |  | CAV_POD_3_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.23 | 3.13 | 3.23 | 3.13 | 3.23
BLD10PRE | EffHeat |  | Heating Efficiency (%) | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PRE |  |  | HEATSYS1 BOILER | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PRE |  |  | PSZ-AC_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PRE |  |  | PSZ-AC_2:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PRE |  |  | PSZ-AC_3:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PRE |  |  | PSZ-AC_4:8_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PRE |  |  | PSZ-AC_5:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PRE |  |  | HVAC Control - Economizer
BLD10PRE |  |  | PSZ-AC_1:5 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PRE |  |  | PSZ-AC_2:6 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PRE |  |  | PSZ-AC_3:7 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PRE |  |  | PSZ-AC_4:8 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD10PRE |  |  | PSZ-AC_5:9 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PRE |  |  | CAV_OTHER | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PRE |  |  | CAV_POD_1 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PRE |  |  | CAV_POD_2 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PRE |  |  | CAV_POD_3 | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 104.57 | 108 | 115.33 | 109.89 | 99.63 | 112.45 | 118.31 | 103.88 | 101.53 | 99.83 | 86.71 | 83.33 | 83.35 | 82.47 | 80.83 | 92.16
BLD10PRE |  |  | BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BLD10PRE |  |  | BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BLD10PRE |  |  | CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63
BLD10PRE |  |  | KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
BLD10PRE |  |  | PSZ-AC_1:5_FAN | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76
BLD10PRE |  |  | PSZ-AC_2:6_FAN | 7.02 | 7.13 | 7.67 | 7.38 | 6.16 | 6.88 | 5.71 | 6.46 | 5.8 | 5.56 | 4.43 | 4.05 | 4.17 | 4.58 | 4.51 | 5.76
BLD10PRE |  |  | PSZ-AC_3:7_FAN | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 8.58 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
BLD10PRE |  |  | PSZ-AC_4:8_FAN | 0.81 | 0.8 | 0.78 | 0.83 | 0.67 | 0.67 | 1.11 | 0.73 | 0.69 | 0.59 | 0.59 | 0.54 | 0.59 | 0.53 | 0.47 | 0.53
BLD10PRE |  |  | PSZ-AC_5:9_FAN | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49
BLD10PRE |  |  | CAV_OTHER_FAN | 20.47 | 21.55 | 23.37 | 21.98 | 18.86 | 22.39 | 21.36 | 19.87 | 19.55 | 17.68 | 15.34 | 14.38 | 13.99 | 14.53 | 14.11 | 17.26
BLD10PRE |  |  | CAV_POD_1_FAN | 13.65 | 14.4 | 16.06 | 14.79 | 12.9 | 15.72 | 18.25 | 13.85 | 13.34 | 13.62 | 10.34 | 9.67 | 9.76 | 9.14 | 8.93 | 11.32
BLD10PRE |  |  | CAV_POD_2_FAN | 13.63 | 14.38 | 16.03 | 14.76 | 12.86 | 15.69 | 18.23 | 13.8 | 13.31 | 13.54 | 10.34 | 9.64 | 9.75 | 9.16 | 8.92 | 11.31
BLD10PRE |  |  | CAV_POD_3_FAN | 14.35 | 15.1 | 16.78 | 15.51 | 13.54 | 16.46 | 18.33 | 14.53 | 14.2 | 14.2 | 11.03 | 10.41 | 10.45 | 9.89 | 9.25 | 11.34
BLD10PRE |  | Utility Costs
BLD10PRE |  |  | Electric Utility Rates
BLD10PRE |  |  | Average Annual Rate ($/kWh) | 0.088251 | 0.11679 | 0.086707 | 0.10256 | 0.064169 | 0.10279 | 0.15466 | 0.078936 | 0.036995 | 0.072163 | 0.084954 | 0.037003 | 0.063316 | 0.078099 | 0.06096 | 0.095167
BLD10PRE |  |  | Total Cost ($/m2) | 18.01 | 21.18 | 17.1 | 16.09 | 8.78 | 18.47 | 19.55 | 11.6 | 5.43 | 9.03 | 11.48 | 4.85 | 8.35 | 9.87 | 7.58 | 12.02
BLD10PRE |  |  | Gas Utility Rates
BLD10PRE |  |  | Average Annual Rate ($/MJ) | 0.011427 | 0.0080772 | 0.008287 | 0.0097172 | 0.0085543 | 0.0077412 | 0.0085552 | 0.0097008 | 0.0069266 | 0.0084011 | 0.0083673 | 0.0069472 | 0.0078752 | 0.0081574 | 0.0078721 | 0.0041315
BLD10PRE |  |  | Total Cost ($/m2) | 0.47 | 1.22 | 0.93 | 2.67 | 0.88 | 1.29 | 1.87 | 4.38 | 2.07 | 3.7 | 4.63 | 2.83 | 5.8 | 4.81 | 7.04 | 6.31
BLD10PRE |  |  | Total Utility Costs
BLD10PRE |  |  | Cost Intensity ($/m2) | 18.48 | 22.4 | 18.03 | 18.76 | 9.66 | 19.75 | 21.42 | 15.98 | 7.5 | 12.74 | 16.12 | 7.68 | 14.15 | 14.67 | 14.62 | 18.33
BLD10PRE |  | Energy - End Uses
BLD10PRE |  |  | Electricity (kWh)
BLD10PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Cooling | 1485355.5556 | 1078897.2222 | 1277694.4444 | 620150 | 320941.6667 | 975619.4444 | 103911.1111 | 453172.2222 | 434122.2222 | 92775 | 296977.7778 | 231252.7778 | 229572.2222 | 131694.4444 | 82738.8889 | 36422.2222
BLD10PRE |  |  | Interior Lighting | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111
BLD10PRE |  |  | Exterior Lighting | 95611.1111 | 95575 | 95555.5556 | 95541.6667 | 95469.4444 | 95447.2222 | 95497.2222 | 95438.8889 | 95475 | 95286.1111 | 95455.5556 | 95400 | 95391.6667 | 95369.4444 | 95316.6667 | 94733.3333
BLD10PRE |  |  | Interior Equipment | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778
BLD10PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Fans | 602627.7778 | 565086.1111 | 675825 | 545269.4444 | 451497.2222 | 635355.5556 | 466283.3333 | 518177.7778 | 535827.7778 | 453325 | 443519.4444 | 429908.3333 | 444261.1111 | 436233.3333 | 445886.1111 | 524038.8889
BLD10PRE |  |  | Pumps | 1027.7778 | 1683.3333 | 1355.5556 | 2380.5556 | 1344.4444 | 1847.2222 | 1661.1111 | 3380.5556 | 2347.2222 | 3336.1111 | 3511.1111 | 2813.8889 | 4947.2222 | 4113.8889 | 6419.4444 | 14294.4444
BLD10PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Refrigeration | 43808.3333 | 41830.5556 | 41972.2222 | 39966.6667 | 40000 | 40636.1111 | 38261.1111 | 38688.8889 | 38725 | 37425 | 37825 | 37602.7778 | 37405.5556 | 36727.7778 | 36058.3333 | 34975
BLD10PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total End Uses | 3999066.6667 | 3553711.1111 | 3863044.4444 | 3073947.2222 | 2679891.6667 | 3519544.4444 | 2476255.5556 | 2879497.2222 | 2877138.8889 | 2452786.1111 | 2647927.7778 | 2567619.4444 | 2582219.4444 | 2474777.7778 | 2437058.3333 | 2475102.7778
BLD10PRE |  |  | Gas (MJ)
BLD10PRE |  |  | Heating | 192610 | 2278930 | 1559320 | 4648960 | 1299520 | 2566040 | 3521020 | 8062710 | 5089300 | 7837360 | 10033570 | 7166100 | 13579960 | 10692830 | 16614430 | 28951490
BLD10PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Equipment | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390
BLD10PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems | 253310 | 319760 | 289350 | 378840 | 358810 | 332760 | 408830 | 425830 | 416800 | 442400 | 465830 | 462090 | 501490 | 504760 | 554730 | 617780
BLD10PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total End Uses | 799310 | 2952090 | 2202060 | 5381190 | 2011720 | 3252190 | 4283240 | 8841930 | 5859500 | 8633150 | 10852790 | 7981590 | 14434840 | 11550990 | 17522550 | 29922670
BLD10PRE |  |  | Purchased Cooling (MJ)
BLD10PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Purchased Heating (MJ)
BLD10PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total Building (MJ) | 15195960 | 15745450 | 16109010 | 16447400 | 11659330 | 15922550 | 13197760 | 19208120 | 16217200 | 17463180 | 20385340 | 17225010 | 23730830 | 20460190 | 26295950 | 38833030
BLD10PRE |  | Energy - End Use Intensities
BLD10PRE |  |  | Electricity (MJ/m2)
BLD10PRE |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Cooling (elec) | 272.9318 | 198.2457 | 234.7744 | 113.9516 | 58.9725 | 179.2686 | 19.0935 | 83.2697 | 79.7693 | 17.0473 | 54.5692 | 42.4923 | 42.1835 | 24.1987 | 15.2031 | 6.6925
BLD10PRE |  |  | Interior Lighting (elec) | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894
BLD10PRE |  |  | Exterior Lighting (elec) | 17.5684 | 17.5618 | 17.5582 | 17.5556 | 17.5424 | 17.5383 | 17.5475 | 17.5367 | 17.5434 | 17.5087 | 17.5398 | 17.5296 | 17.5281 | 17.524 | 17.5143 | 17.4071
BLD10PRE |  |  | Interior Equipment (elec) | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628
BLD10PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Fans (elec) | 110.7319 | 103.8337 | 124.1818 | 100.1924 | 82.9619 | 116.7456 | 85.6788 | 95.2144 | 98.4575 | 83.2978 | 81.496 | 78.995 | 81.6323 | 80.1572 | 81.9309 | 96.2913
BLD10PRE |  |  | Pumps (elec) | 0.18885 | 0.30931 | 0.24908 | 0.43742 | 0.24704 | 0.33942 | 0.30523 | 0.62117 | 0.4313 | 0.61301 | 0.64516 | 0.51705 | 0.90904 | 0.75592 | 1.1796 | 2.6266
BLD10PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Refrigeration (elec) | 8.0497 | 7.6863 | 7.7123 | 7.3438 | 7.3499 | 7.4668 | 7.0304 | 7.109 | 7.1157 | 6.8768 | 6.9503 | 6.9095 | 6.8732 | 6.7487 | 6.6257 | 6.4266
BLD10PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total End Uses | 734.8224 | 652.989 | 709.8285 | 564.8331 | 492.426 | 646.7109 | 455.0082 | 529.1032 | 528.6699 | 450.6957 | 486.5527 | 471.7961 | 474.4789 | 454.7366 | 447.8057 | 454.7963
BLD10PRE |  |  | Gas (MJ/m2)
BLD10PRE |  |  | Heating (gas) | 9.8311 | 116.3194 | 79.5896 | 237.2887 | 66.3291 | 130.9739 | 179.7172 | 411.5307 | 259.7642 | 400.0286 | 512.1259 | 365.7666 | 693.138 | 545.7753 | 848.0211 | 1477.72
BLD10PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Equipment (gas) | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375
BLD10PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems (gas) | 12.9293 | 16.3209 | 14.7688 | 19.3365 | 18.3141 | 16.9845 | 20.8672 | 21.7349 | 21.274 | 22.5806 | 23.7765 | 23.5856 | 25.5967 | 25.7636 | 28.3141 | 31.5323
BLD10PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total End Uses | 40.7978 | 150.6783 | 112.3959 | 274.6626 | 102.6807 | 165.9958 | 218.6219 | 451.3031 | 299.0762 | 440.6467 | 553.9399 | 407.3903 | 736.7722 | 589.5769 | 894.3727 | 1527.2902
BLD10PRE |  |  | Purchased Cooling (MJ/m2)
BLD10PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Purchased Heating (MJ/m2)
BLD10PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Total Building (MJ/m2) | 775.6207 | 803.6673 | 822.2239 | 839.4957 | 595.1067 | 812.7067 | 673.6301 | 980.4063 | 827.746 | 891.3424 | 1040.4931 | 879.1859 | 1211.251 | 1044.3135 | 1342.1779 | 1982.0861
BLD10PRE |  | Peak Energy Demand
BLD10PRE |  |  | Electricity Peak Demand (kW)
BLD10PRE |  |  | Jan | 1058.408 | 960.4244 | 836.5141 | 680.8691 | 892.6912 | 667.1318 | 592.2459 | 557.338 | 603.3312 | 525.8532 | 527.1426 | 577.1035 | 520.5775 | 535.8172 | 522.0342 | 552.3412
BLD10PRE |  |  | Feb | 1111.6655 | 979.6826 | 940.1784 | 647.0816 | 853.6298 | 728.4969 | 717.0552 | 570.3899 | 712.2921 | 574.1872 | 526.2614 | 560.6395 | 516.1141 | 565.2479 | 519.1496 | 544.0235
BLD10PRE |  |  | Mar | 1145.0332 | 963.5088 | 1150.3809 | 834.4928 | 825.5455 | 843.9472 | 652.1248 | 792.7546 | 732.1304 | 656.0629 | 646.9382 | 712.255 | 562.6903 | 647.0465 | 516.5951 | 543.5946
BLD10PRE |  |  | Apr | 1209.2191 | 1080.83 | 1176.0853 | 978.9292 | 938.1109 | 1147.0707 | 759.1001 | 812.5205 | 932.9766 | 604.8459 | 665.1687 | 780.9435 | 650.244 | 606.2536 | 558.9929 | 523.3377
BLD10PRE |  |  | May | 1302.2456 | 1334.6413 | 1384.8181 | 1152.0596 | 908.4109 | 1326.7142 | 805.9931 | 1045.4926 | 1057.7311 | 789.1418 | 988.2313 | 904.4244 | 962.632 | 762.0593 | 721.5231 | 633.7619
BLD10PRE |  |  | Jun | 1335.2876 | 1354.179 | 1683.8935 | 1291.2338 | 874.0026 | 1554.1973 | 833.5614 | 1334.7959 | 1158.2339 | 862.8243 | 1194.1128 | 1031.2585 | 1127.7429 | 980.3506 | 953.9116 | 806.6488
BLD10PRE |  |  | Jul | 1073.8943 | 1153.1484 | 1400.7114 | 1172.2156 | 656.6441 | 1327.1551 | 712.7777 | 1155.3322 | 998.852 | 728.0274 | 982.472 | 831.9733 | 898.904 | 764.5986 | 767.0702 | 550.6343
BLD10PRE |  |  | Aug | 1134.5055 | 1162.4099 | 1415.5557 | 1074.057 | 781.0552 | 1266.2698 | 650.7315 | 1146.5026 | 942.0978 | 671.3042 | 962.1768 | 849.2786 | 873.8079 | 714.5621 | 697.2663 | 530.6009
BLD10PRE |  |  | Sep | 1303.6894 | 1340.5357 | 1501.4536 | 1237.0019 | 1058.8719 | 1351.8619 | 1114.8625 | 1163.4842 | 1016.4362 | 916.9701 | 1004.1953 | 976.6281 | 958.8776 | 815.7368 | 837.0791 | 553.7521
BLD10PRE |  |  | Oct | 1266.5806 | 1170.5275 | 1192.2616 | 1082.0462 | 988.8827 | 1157.4801 | 813.0178 | 955.2164 | 910.7723 | 690.2212 | 779.1255 | 887.5898 | 679.732 | 713.8031 | 584.6949 | 542.3443
BLD10PRE |  |  | Nov | 1161.1827 | 1026.0498 | 1065.447 | 749.5414 | 890.5575 | 780.9775 | 634.6505 | 835.0328 | 671.1334 | 534.9693 | 768.7096 | 652.2692 | 596.6053 | 534.7405 | 527.3273 | 547.5842
BLD10PRE |  |  | Dec | 1033.2796 | 966.1864 | 798.5076 | 659.9995 | 924.4536 | 743.0694 | 606.6564 | 530.8518 | 589.6416 | 526.0365 | 517.9292 | 551.1769 | 516.9546 | 535.4817 | 518.1307 | 551.7244
BLD10PRE |  |  | Time of Peak Electrical Demand
BLD10PRE |  |  | Jan | 06-JAN-12:00 | 03-JAN-12:00 | 26-JAN-15:00 | 23-JAN-14:39 | 26-JAN-12:00 | 18-JAN-14:00 | 17-JAN-14:30 | 05-JAN-13:00 | 25-JAN-14:00 | 03-JAN-16:40 | 17-JAN-12:00 | 27-JAN-11:50 | 04-JAN-16:00 | 06-JAN-08:09 | 09-JAN-16:40 | 03-JAN-11:09
BLD10PRE |  |  | Feb | 23-FEB-11:00 | 23-FEB-15:09 | 28-FEB-16:10 | 27-FEB-14:00 | 13-FEB-11:00 | 08-FEB-14:30 | 15-FEB-15:00 | 15-FEB-14:30 | 14-FEB-15:00 | 21-FEB-13:30 | 28-FEB-11:39 | 07-FEB-14:00 | 01-FEB-11:09 | 02-FEB-14:00 | 01-FEB-10:09 | 03-FEB-09:30
BLD10PRE |  |  | Mar | 13-MAR-15:09 | 29-MAR-11:00 | 17-MAR-14:00 | 28-MAR-15:00 | 30-MAR-11:00 | 31-MAR-15:30 | 01-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 29-MAR-15:30 | 31-MAR-14:00 | 30-MAR-15:00 | 23-MAR-13:00 | 30-MAR-15:00 | 07-MAR-11:09 | 14-MAR-07:19
BLD10PRE |  |  | Apr | 17-APR-12:00 | 17-APR-15:39 | 26-APR-15:50 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:30 | 13-APR-14:00 | 04-APR-15:00 | 21-APR-15:00 | 14-APR-13:00 | 07-APR-14:09 | 25-APR-14:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 25-APR-13:00
BLD10PRE |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:00 | 15-MAY-14:00 | 30-MAY-11:20 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:30 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-11:00 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-14:00
BLD10PRE |  |  | Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-13:00 | 20-JUN-13:00 | 28-JUN-12:00 | 08-JUN-12:00 | 28-JUN-11:00 | 29-JUN-15:09 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-15:00
BLD10PRE |  |  | Jul | 10-JUL-13:30 | 18-JUL-12:50 | 11-JUL-15:00 | 03-JUL-14:00 | 24-JUL-13:50 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-11:00 | 17-JUL-14:00 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-14:00 | 21-JUL-16:00
BLD10PRE |  |  | Aug | 21-AUG-13:00 | 31-AUG-13:00 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 04-AUG-14:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 04-AUG-14:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-14:00 | 15-AUG-13:00
BLD10PRE |  |  | Sep | 07-SEP-13:00 | 15-SEP-14:00 | 08-SEP-13:00 | 11-SEP-13:50 | 25-SEP-11:00 | 20-SEP-15:39 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-15:09 | 13-SEP-14:00 | 06-SEP-11:50 | 06-SEP-15:20 | 14-SEP-14:00 | 07-SEP-15:00 | 07-SEP-14:00 | 07-SEP-13:00
BLD10PRE |  |  | Oct | 06-OCT-13:00 | 06-OCT-15:00 | 24-OCT-14:39 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 31-OCT-12:00 | 03-OCT-14:09 | 13-OCT-14:00 | 17-OCT-12:00 | 31-OCT-11:00 | 05-OCT-15:09 | 06-OCT-14:00 | 06-OCT-15:00 | 27-OCT-11:00 | 30-OCT-07:10
BLD10PRE |  |  | Nov | 01-NOV-11:00 | 03-NOV-14:30 | 13-NOV-14:30 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-12:00 | 08-NOV-12:00 | 03-NOV-13:00 | 08-NOV-15:09 | 03-NOV-10:09 | 02-NOV-14:30 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-12:00 | 09-NOV-12:00 | 27-NOV-10:09
BLD10PRE |  |  | Dec | 19-DEC-12:00 | 19-DEC-15:09 | 11-DEC-15:30 | 01-DEC-14:30 | 19-DEC-12:00 | 05-DEC-13:00 | 07-DEC-12:00 | 08-DEC-11:39 | 05-DEC-14:09 | 26-DEC-16:19 | 14-DEC-16:00 | 21-DEC-14:09 | 29-DEC-16:00 | 18-DEC-08:09 | 11-DEC-10:20 | 29-DEC-11:09
BLD10PRE |  | Source Energy
BLD10PRE |  |  | Total Source Energy (GJ) | 48626.52 | 49689.16 | 46392.35 | 43103 | 32056.16 | 48873.27 | 32267.73 | 46724.88 | 40765.44 | 24809.32 | 45653.65 | 39385.58 | 47713.17 | 43582.07 | 49288.82 | 64503.39
BLD10PRE |  |  | Total Source Energy (MJ/m2) | 2481.96 | 2536.2 | 2367.92 | 2200.03 | 1636.19 | 2494.55 | 1646.99 | 2384.9 | 2080.72 | 1266.3 | 2330.22 | 2010.29 | 2435.34 | 2224.48 | 2515.76 | 3292.33
BLD10PRE |  | Water Consumption (m3)
BLD10PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Water Systems | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
BLD10PRE |  |  | Total Building | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
BLD10PRE |  | Emissions
BLD10PRE |  |  | Carbon Equivalent (kg) | 1111160 | 1238610 | 1205870 | 1043930 | 349464.5379 | 1245700 | 366628.0111 | 936492.0416 | 1280970 | 334325.6746 | 1607450 | 1192800 | 1144170 | 1112670 | 1150170 | 1236050
BLD10PRE |  |  | CO2 (kg) | 2581210 | 3128260 | 2857180 | 2429420 | 940969.1407 | 2980990 | 995778.1579 | 2203220 | 3043860 | 874158.5395 | 3822700 | 2859800 | 2789740 | 2705270 | 2836060 | 3303620
BLD10PRE |  |  | NOX (kg) | 4516.6033 | 4049.2845 | 4739.3455 | 4404.3597 | 810.7177 | 4764.5724 | 863.7871 | 3902.2999 | 5082.0934 | 1090.2031 | 6444.4848 | 4665.5542 | 4401.1638 | 4280.2091 | 4338.1786 | 3601.0556
BLD10PRE |  |  | SO2 (kg) | 17117.8232 | 16951.993 | 15534.6591 | 10790.9984 | 7798.7036 | 19361.1806 | 7206.7521 | 10513.6869 | 12565.466 | 1898.1214 | 17847.8272 | 11214.4143 | 6098.319 | 6611.0524 | 5756.5404 | 12607.2811
BLD10PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PRE |  |  | Hg (kg) | 0.0781 | 0.0479 | 0.0424 | 0.0399 | 0.0037 | 0.0366 | 0.0037 | 0.0433 | 0.0496 | 0.0083 | 0.055 | 0.0445 | 0.046 | 0.0471 | 0.0439 | 0.0459
BLD10PRE |  |  | Water for Electricity (m3) | 2118.54 | 5782.3 | 114749 | 19192.5 | 47052.9 | 96555.2 | 43477.5 | 653.7542 | 13064.5 | 25059.6 | 4108.1 | 11659 | 4006.16 | 156763 | 3780.95 | 2528.76
BLD10PST |  | Program
BLD10PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD10PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD10PST |  |  | Weighting Factor
BLD10PST |  | Fabric
BLD10PST |  |  | Exterior walls
BLD10PST | TypeWall |  | Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
BLD10PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD10PST |  |  | Roof
BLD10PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD10PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD10PST |  |  | Window
BLD10PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD10PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD10PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD10PST |  |  | Skylights/TDD
BLD10PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD10PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD10PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD10PST |  |  | Foundation
BLD10PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD10PST |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD10PST |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD10PST |  | HVAC
BLD10PST |  |  | HVAC Sizing
BLD10PST | HVAC |  | Air Conditioning (kW) | 2737.6387 | 2516.7278 | 2298.9302 | 2331.4039 | 2089.1321 | 1962.1853 | 1789.8304 | 2268.0383 | 1516.1452 | 1556.6179 | 2247.5348 | 1462.067 | 2126.4841 | 1273.6199 | 1908.3818 | 1286.6883
BLD10PST |  |  | COOLSYS1 CHILLER | 1761.9664 | 1589.1498 | 1359.4072 | 1405.0212 | 1150.8386 | 1053.1397 | 1087.4391 | 1362.4845 | 736.8464 | 803.0882 | 1342.0553 | 683.1461 | 1221.2478 | 604.5162 | 1003.5732 | 667.9734
BLD10PST |  |  | PSZ-AC_1:5_COOLC DXCOIL | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 360.1228 | 490.6879 | 429.2239 | 413.8807 | 490.6879 | 431.1614 | 490.6879 | 363.8108 | 490.6879 | 327.0982
BLD10PST |  |  | PSZ-AC_2:6_COOLC DXCOIL | 158.0154 | 113.6429 | 125.6197 | 112.9146 | 124.6795 | 97.4669 | 88.9148 | 93.0655 | 84.3292 | 83.6488 | 93.0655 | 84.8786 | 93.0655 | 75.9789 | 94.4359 | 78.5496
BLD10PST |  |  | PSZ-AC_3:7_COOLC DXCOIL | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 146.5271 | 196.2751 | 150.7166 | 155.768 | 196.2751 | 147.6431 | 196.2751 | 130.8393 | 196.2751 | 130.8393
BLD10PST |  |  | PSZ-AC_4:8_COOLC DXCOIL | 19.2162 | 15.4944 | 15.4625 | 15.0274 | 15.1732 | 13.138 | 20.6645 | 14.0475 | 12.7934 | 10.2 | 13.9732 | 12.2685 | 13.73 | 10.0339 | 11.932 | 7.9155
BLD10PST |  |  | PSZ-AC_5:9_COOLC DXCOIL | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 86.162 | 111.4777 | 102.2356 | 90.0322 | 111.4777 | 102.9694 | 111.4777 | 88.4408 | 111.4777 | 74.3123
BLD10PST | HEAT |  | Heating (kW) | 2353.5783 | 2780.2315 | 2429.2666 | 2953.7438 | 2348.8006 | 2497.6382 | 2727.5954 | 3131.6899 | 2518.2427 | 2767.3755 | 3621.3014 | 2887.0059 | 3827.022 | 3507.8012 | 3909.3425 | 5119.3991
BLD10PST |  |  | HEATSYS1 BOILER | 873.5509 | 894.4463 | 825.3552 | 923.2742 | 840.5877 | 795.6681 | 1054.6365 | 893.5487 | 740.4396 | 837.4034 | 1006.9049 | 766.4241 | 1002.3871 | 932.1343 | 1022.6503 | 1523.8295
BLD10PST |  |  | PSZ-AC_1:5_HEATC | 765.0269 | 1009.9404 | 852.0818 | 1089.4655 | 795.6607 | 921.1228 | 879.4681 | 1212.7703 | 963.6127 | 1048.8159 | 1416.7661 | 1150.2765 | 1531.1076 | 1395.2101 | 1567.2052 | 1940.738
BLD10PST |  |  | PSZ-AC_2:6_HEATC | 205.2261 | 210.5328 | 190.5644 | 224.3407 | 188.9209 | 178.4688 | 193.2796 | 230.0181 | 182.762 | 198.9219 | 268.7086 | 218.1653 | 290.395 | 269.6886 | 298.4473 | 390.6621
BLD10PST |  |  | PSZ-AC_3:7_HEATC | 306.0108 | 403.9762 | 340.8327 | 435.7862 | 318.2643 | 368.4491 | 353.2187 | 485.1081 | 385.4451 | 419.5263 | 566.7064 | 460.1106 | 612.443 | 558.084 | 626.8821 | 776.2952
BLD10PST |  |  | PSZ-AC_4:8_HEATC | 29.9597 | 31.8908 | 26.8508 | 33.3651 | 24.6036 | 24.6627 | 47.1892 | 34.7194 | 27.0634 | 24.431 | 40.345 | 30.7018 | 42.8421 | 35.711 | 38.1094 | 46.9644
BLD10PST |  |  | PSZ-AC_5:9_HEATC | 173.8039 | 229.445 | 193.5816 | 247.512 | 180.7635 | 209.2668 | 199.8034 | 275.5253 | 218.92 | 238.277 | 321.8704 | 261.3275 | 347.8472 | 316.9731 | 356.0481 | 440.9098
BLD10PST |  |  | HVAC Efficiency
BLD10PST | COP |  | Air Conditioning (COP) | 2.7441 | 2.7523 | 2.78 | 2.7719 | 2.8076 | 2.8161 | 2.7695 | 2.7726 | 2.8506 | 2.8297 | 2.775 | 2.8631 | 2.7905 | 2.8584 | 2.8231 | 2.8283
BLD10PST |  |  | COOLSYS1 CHILLER | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
BLD10PST |  |  | PSZ-AC_1:5_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD10PST |  |  | PSZ-AC_2:6_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD10PST |  |  | PSZ-AC_3:7_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD10PST |  |  | PSZ-AC_4:8_COOLC DXCOIL | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD10PST |  |  | PSZ-AC_5:9_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD10PST | EffHeat |  | Heating Efficiency (%) | 0.75056 | 0.75449 | 0.75304 | 0.75522 | 0.75158 | 0.75471 | 0.74941 | 0.7574 | 0.75669 | 0.75597 | 0.75798 | 0.75897 | 0.75927 | 0.75895 | 0.75927 | 0.75637
BLD10PST |  |  | HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
BLD10PST |  |  | PSZ-AC_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PST |  |  | PSZ-AC_2:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PST |  |  | PSZ-AC_3:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PST |  |  | PSZ-AC_4:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD10PST |  |  | PSZ-AC_5:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10PST |  |  | HVAC Control - Economizer
BLD10PST |  |  | PSZ-AC_1:5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PST |  |  | PSZ-AC_2:6_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PST |  |  | PSZ-AC_3:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PST |  |  | PSZ-AC_4:8_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD10PST |  |  | PSZ-AC_5:9_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PST |  |  | VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PST |  |  | VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PST |  |  | VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PST |  |  | VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10PST | Fan |  | Fan Max Flow Rate (m3/s ) | 99.42 | 86.6 | 90.06 | 85.45 | 94.3 | 84.54 | 102.97 | 79.08 | 80.14 | 81.24 | 78.3 | 75.07 | 75.15 | 76.03 | 75.18 | 83.63
BLD10PST |  |  | BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BLD10PST |  |  | BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BLD10PST |  |  | CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63
BLD10PST |  |  | KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
BLD10PST |  |  | PSZ-AC_1:5_FAN | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76
BLD10PST |  |  | PSZ-AC_2:6_FAN | 6.36 | 4.58 | 5.06 | 4.55 | 5.41 | 3.92 | 4.9 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 3.75 | 4 | 3.8 | 4.75
BLD10PST |  |  | PSZ-AC_3:7_FAN | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.97 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
BLD10PST |  |  | PSZ-AC_4:8_FAN | 0.77 | 0.62 | 0.62 | 0.61 | 0.61 | 0.53 | 1.06 | 0.57 | 0.55 | 0.46 | 0.56 | 0.53 | 0.55 | 0.51 | 0.48 | 0.48
BLD10PST |  |  | PSZ-AC_5:9_FAN | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49
BLD10PST |  |  | VAV_OTHER_FAN | 18.88 | 15.42 | 15.31 | 15.3 | 17.62 | 13.97 | 17.74 | 13.12 | 13.34 | 12.87 | 12.63 | 11.44 | 11.49 | 12.77 | 11.87 | 14.02
BLD10PST |  |  | VAV_POD_1_FAN | 12.69 | 10.21 | 11.23 | 9.87 | 11.81 | 10.24 | 14.8 | 8.77 | 9.08 | 9.64 | 8.68 | 8.04 | 8.02 | 7.83 | 7.91 | 9.75
BLD10PST |  |  | VAV_POD_2_FAN | 12.7 | 10.24 | 11.26 | 9.91 | 11.79 | 10.27 | 14.85 | 8.79 | 9.01 | 9.63 | 8.69 | 7.96 | 8.03 | 7.82 | 7.91 | 9.65
BLD10PST |  |  | VAV_POD_3_FAN | 13.38 | 10.89 | 11.94 | 10.57 | 12.42 | 10.97 | 14.91 | 9.44 | 9.77 | 10.25 | 9.35 | 8.71 | 8.67 | 8.46 | 8.57 | 10.34
BLD10PST |  | Utility Costs
BLD10PST |  |  | Electric Utility Rates
BLD10PST |  |  | Average Annual Rate ($/kWh) | 0.080425 | 0.11145 | 0.077084 | 0.099095 | 0.06016 | 0.098237 | 0.16728 | 0.079896 | 0.036989 | 0.074548 | 0.083442 | 0.036996 | 0.065017 | 0.079515 | 0.064306 | 0.09763
BLD10PST |  |  | Total Cost ($/m2) | 28.15 | 30.24 | 22.08 | 21.06 | 11.61 | 22.01 | 24.81 | 15.04 | 5.98 | 9.99 | 14.18 | 5.36 | 10.41 | 10.66 | 8.65 | 12.53
BLD10PST |  |  | Gas Utility Rates
BLD10PST |  |  | Average Annual Rate ($/MJ) | 0.011425 | 0.0080772 | 0.0082761 | 0.0097027 | 0.0085578 | 0.0077355 | 0.008564 | 0.0096991 | 0.0069192 | 0.0084079 | 0.0083544 | 0.0069408 | 0.0078754 | 0.0081409 | 0.007869 | 0.004129
BLD10PST |  |  | Total Cost ($/m2) | 0.49 | 1.15 | 0.9 | 2.43 | 0.87 | 1.19 | 1.9 | 3.81 | 1.89 | 3.22 | 4.37 | 2.62 | 5.39 | 4.51 | 6.45 | 5.84
BLD10PST |  |  | Total Utility Costs
BLD10PST |  |  | Cost Intensity ($/m2) | 28.63 | 31.4 | 22.98 | 23.48 | 12.48 | 23.21 | 26.71 | 18.85 | 7.87 | 13.21 | 18.55 | 7.99 | 15.8 | 15.18 | 15.1 | 18.37
BLD10PST |  | Energy - End Uses
BLD10PST |  |  | Electricity (kWh)
BLD10PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Cooling | 4551300 | 3073322.2222 | 3333666.6667 | 1937619.4444 | 1559802.7778 | 2143322.2222 | 702563.8889 | 1473866.6667 | 935922.2222 | 436844.4444 | 1108955.5556 | 624452.7778 | 910866.6667 | 406597.2222 | 407308.3333 | 235211.1111
BLD10PST |  |  | Interior Lighting | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111 | 1137911.1111
BLD10PST |  |  | Exterior Lighting | 95611.1111 | 95575 | 95555.5556 | 95541.6667 | 95469.4444 | 95447.2222 | 95497.2222 | 95438.8889 | 95475 | 95286.1111 | 95455.5556 | 95400 | 95391.6667 | 95369.4444 | 95316.6667 | 94733.3333
BLD10PST |  |  | Interior Equipment | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778
BLD10PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Fans | 371638.8889 | 321463.8889 | 355358.3333 | 309730.5556 | 308336.1111 | 329916.6667 | 294447.2222 | 300969.4444 | 317477.7778 | 282516.6667 | 309930.5556 | 307147.2222 | 314866.6667 | 312988.8889 | 318880.5556 | 368716.6667
BLD10PST |  |  | Pumps | 23536.1111 | 13561.1111 | 14411.1111 | 9483.3333 | 7177.7778 | 10675 | 3761.1111 | 7341.6667 | 7013.8889 | 3266.6667 | 6402.7778 | 4911.1111 | 6719.4444 | 4930.5556 | 5591.6667 | 9036.1111
BLD10PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Refrigeration | 43705.5556 | 41716.6667 | 41830.5556 | 39866.6667 | 39922.2222 | 40483.3333 | 38211.1111 | 38680.5556 | 38644.4444 | 37430.5556 | 37838.8889 | 37625 | 37455.5556 | 36766.6667 | 36186.1111 | 35227.7778
BLD10PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total End Uses | 6856430.5556 | 5316275 | 5611461.1111 | 4162883.3333 | 3781344.4444 | 4390486.1111 | 2905119.4444 | 3686936.1111 | 3165172.2222 | 2625983.3333 | 3329225 | 2840172.2222 | 3135938.8889 | 2627294.4444 | 2633919.4444 | 2513563.8889
BLD10PST |  |  | Gas (MJ)
BLD10PST |  |  | Heating | 218680 | 2116720 | 1474300 | 4158260 | 1265080 | 2327100 | 3577440 | 6906370 | 4572220 | 6702380 | 9415420 | 6575680 | 12545750 | 9994050 | 15148620 | 26730970
BLD10PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Equipment | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390
BLD10PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems | 259790 | 327950 | 296780 | 388530 | 367990 | 341320 | 419270 | 436740 | 427470 | 453760 | 477760 | 473930 | 514340 | 517700 | 568950 | 633610
BLD10PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total End Uses | 831870 | 2798060 | 2124480 | 4900190 | 1986470 | 3021810 | 4350110 | 7696500 | 5353080 | 7509530 | 10246570 | 7403000 | 13413480 | 10865140 | 16070960 | 27717980
BLD10PST |  |  | Purchased Cooling (MJ)
BLD10PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Purchased Heating (MJ)
BLD10PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total Building (MJ) | 25515020 | 21936650 | 22325740 | 19886570 | 15599310 | 18827550 | 14808540 | 20969470 | 16747700 | 16963060 | 22231780 | 17627620 | 24702860 | 20323400 | 25553070 | 36766810
BLD10PST |  | Energy - End Use Intensities
BLD10PST |  |  | Electricity (MJ/m2)
BLD10PST |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Cooling (elec) | 836.2944 | 564.7183 | 612.5561 | 356.0346 | 286.6114 | 393.8322 | 129.095 | 270.8207 | 171.9743 | 80.2695 | 203.7689 | 114.7422 | 167.3704 | 74.7116 | 74.8423 | 43.2197
BLD10PST |  |  | Interior Lighting (elec) | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894 | 209.0894
BLD10PST |  |  | Exterior Lighting (elec) | 17.5684 | 17.5618 | 17.5582 | 17.5556 | 17.5424 | 17.5383 | 17.5475 | 17.5367 | 17.5434 | 17.5087 | 17.5398 | 17.5296 | 17.5281 | 17.524 | 17.5143 | 17.4071
BLD10PST |  |  | Interior Equipment (elec) | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628
BLD10PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Fans (elec) | 68.2881 | 59.0685 | 65.2965 | 56.9125 | 56.6563 | 60.6217 | 54.1042 | 55.3027 | 58.3361 | 51.912 | 56.9493 | 56.4378 | 57.8563 | 57.5112 | 58.5938 | 67.7511
BLD10PST |  |  | Pumps (elec) | 4.3247 | 2.4918 | 2.648 | 1.7425 | 1.3189 | 1.9615 | 0.6911 | 1.349 | 1.2888 | 0.60024 | 1.1765 | 0.90241 | 1.2347 | 0.90598 | 1.0275 | 1.6604
BLD10PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Refrigeration (elec) | 8.0308 | 7.6654 | 7.6863 | 7.3254 | 7.3356 | 7.4388 | 7.0212 | 7.1075 | 7.1009 | 6.8778 | 6.9528 | 6.9135 | 6.8824 | 6.7558 | 6.6491 | 6.4731
BLD10PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total End Uses | 1259.8586 | 976.8574 | 1031.0974 | 764.9234 | 694.8163 | 806.7451 | 533.8112 | 677.4689 | 581.5955 | 482.5204 | 611.74 | 521.8773 | 576.224 | 482.7613 | 483.9787 | 461.8635
BLD10PST |  |  | Gas (MJ/m2)
BLD10PST |  |  | Heating (gas) | 11.1617 | 108.04 | 75.2501 | 212.2428 | 64.5713 | 118.7781 | 182.597 | 352.5097 | 233.3718 | 342.0978 | 480.5747 | 335.6309 | 640.3507 | 510.1087 | 773.2044 | 1364.3819
BLD10PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Equipment (gas) | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375
BLD10PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems (gas) | 13.26 | 16.739 | 15.148 | 19.8311 | 18.7827 | 17.4214 | 21.4001 | 22.2918 | 21.8186 | 23.1605 | 24.3855 | 24.19 | 26.2526 | 26.4241 | 29.0399 | 32.3402
BLD10PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total End Uses | 42.4597 | 142.8165 | 108.4361 | 250.1118 | 101.3919 | 154.2369 | 222.035 | 392.8389 | 273.2278 | 383.2957 | 522.9977 | 377.8583 | 684.6407 | 554.5702 | 820.2817 | 1414.7601
BLD10PST |  |  | Purchased Cooling (MJ/m2)
BLD10PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Purchased Heating (MJ/m2)
BLD10PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Total Building (MJ/m2) | 1302.3183 | 1119.6738 | 1139.5335 | 1015.0352 | 796.2081 | 960.9815 | 755.8463 | 1070.3078 | 854.8234 | 865.8156 | 1134.7376 | 899.7356 | 1260.8646 | 1037.3316 | 1304.2604 | 1876.6236
BLD10PST |  | Peak Energy Demand
BLD10PST |  |  | Electricity Peak Demand (kW)
BLD10PST |  |  | Jan | 1469.9004 | 1373.8124 | 1257.9236 | 1036.0354 | 1159.6461 | 1006.4722 | 733.197 | 660.0436 | 768.1339 | 497.4134 | 499.7815 | 828.6791 | 500.9316 | 514.6456 | 500.7474 | 528.8871
BLD10PST |  |  | Feb | 1491.3745 | 1457.2958 | 1305.329 | 968.1622 | 1139.7722 | 1049.7766 | 1056.5465 | 665.9252 | 879.1727 | 752.375 | 497.4924 | 691.8965 | 498.2147 | 778.1539 | 499.9397 | 520.6263
BLD10PST |  |  | Mar | 1549.6171 | 1400.0177 | 1396.7799 | 1282.8601 | 1133.7476 | 1104.5977 | 983.4384 | 1274.179 | 879.8545 | 897.8619 | 1198.107 | 878.3294 | 787.6025 | 809.4093 | 497.288 | 520.2751
BLD10PST |  |  | Apr | 1552.8254 | 1458.9458 | 1420.2146 | 1342.0537 | 1214.1178 | 1224.3181 | 1061.9484 | 1264.9762 | 970.7453 | 873.4263 | 1192.3911 | 898.8042 | 1148.6498 | 799.2528 | 831.4676 | 501.55
BLD10PST |  |  | May | 1594.2732 | 1488.3439 | 1493.7461 | 1364.3944 | 1133.5256 | 1297.0098 | 1090.8695 | 1279.6567 | 1026.173 | 948.5119 | 1338.6015 | 968.2563 | 1238.9482 | 859.0457 | 1052.9638 | 820.167
BLD10PST |  |  | Jun | 1621.4259 | 1508.7077 | 1599.3398 | 1417.6336 | 1137.0661 | 1385.1687 | 1110.2551 | 1400.4977 | 1073.0065 | 961.8629 | 1365.0981 | 1035.1247 | 1309.1851 | 997.5502 | 1108.818 | 889.2456
BLD10PST |  |  | Jul | 1415.0497 | 1353.2127 | 1398.8129 | 1246.1615 | 971.9378 | 1186.401 | 981.7252 | 1201.3717 | 894.3573 | 812.4802 | 1186.4422 | 856.459 | 1069.8321 | 781.5743 | 931.8992 | 687.2554
BLD10PST |  |  | Aug | 1416.4653 | 1347.2741 | 1430.4134 | 1204.229 | 1003.6154 | 1179.9722 | 972.0332 | 1207.6106 | 871.0077 | 785.0057 | 1136.8981 | 854.5741 | 1053.7509 | 754.251 | 913.3949 | 681.6807
BLD10PST |  |  | Sep | 1586.0351 | 1492.3381 | 1519.1166 | 1370.4914 | 1231.0517 | 1295.5077 | 1195.5275 | 1391.5899 | 1002.7529 | 985.4405 | 1370.1398 | 997.3808 | 1227.5577 | 892.3692 | 1054.5535 | 788.5517
BLD10PST |  |  | Oct | 1553.488 | 1487.6001 | 1420.8801 | 1409.0782 | 1216.2495 | 1225.9864 | 1093.1159 | 1334.3226 | 952.6343 | 907.0742 | 1262.0877 | 952.4686 | 1159.0415 | 830.342 | 980.1105 | 515.5308
BLD10PST |  |  | Nov | 1517.8133 | 1402.4661 | 1360.5941 | 1234.1861 | 1157.517 | 1065.3064 | 989.8047 | 1209.5026 | 863.5641 | 720.3759 | 1214.9017 | 838.3698 | 1046.7795 | 596.2996 | 514.5072 | 521.3364
BLD10PST |  |  | Dec | 1498.2604 | 1388.8832 | 1250.6454 | 1070.0336 | 1167.005 | 1036.966 | 761.8116 | 497.4543 | 686.2465 | 497.4695 | 497.7069 | 629.13 | 498.358 | 514.2662 | 499.059 | 528.3662
BLD10PST |  |  | Time of Peak Electrical Demand
BLD10PST |  |  | Jan | 06-JAN-12:00 | 02-JAN-16:19 | 26-JAN-16:10 | 23-JAN-15:00 | 26-JAN-12:00 | 18-JAN-15:09 | 27-JAN-14:00 | 09-JAN-11:00 | 26-JAN-15:00 | 27-JAN-16:00 | 27-JAN-16:00 | 27-JAN-11:39 | 04-JAN-16:00 | 05-JAN-08:09 | 09-JAN-16:40 | 03-JAN-11:09
BLD10PST |  |  | Feb | 24-FEB-12:00 | 23-FEB-16:19 | 28-FEB-16:00 | 17-FEB-14:00 | 13-FEB-11:00 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-15:00 | 14-FEB-16:10 | 21-FEB-13:00 | 01-FEB-16:00 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:50 | 01-FEB-11:09 | 03-FEB-08:09
BLD10PST |  |  | Mar | 13-MAR-15:00 | 27-MAR-15:09 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-10:50 | 31-MAR-15:00 | 20-MAR-14:00 | 09-MAR-16:10 | 02-MAR-16:10 | 29-MAR-15:00 | 31-MAR-14:00 | 30-MAR-15:00 | 23-MAR-14:00 | 30-MAR-15:00 | 07-MAR-11:09 | 14-MAR-07:10
BLD10PST |  |  | Apr | 24-APR-13:00 | 28-APR-15:30 | 26-APR-15:39 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 13-APR-15:09 | 04-APR-15:00 | 21-APR-15:00 | 14-APR-13:20 | 07-APR-14:39 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 24-APR-11:00
BLD10PST |  |  | May | 24-MAY-15:20 | 26-MAY-15:30 | 30-MAY-15:00 | 12-MAY-15:00 | 30-MAY-08:00 | 31-MAY-15:00 | 09-MAY-11:00 | 10-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 04-MAY-15:00 | 23-MAY-15:00 | 15-MAY-15:20 | 16-MAY-15:00 | 31-MAY-15:00 | 25-MAY-11:30
BLD10PST |  |  | Jun | 09-JUN-15:00 | 13-JUN-15:09 | 28-JUN-15:00 | 19-JUN-15:30 | 29-JUN-15:00 | 27-JUN-15:00 | 16-JUN-10:09 | 23-JUN-15:00 | 29-JUN-13:00 | 28-JUN-15:20 | 06-JUN-15:00 | 28-JUN-11:00 | 30-JUN-15:20 | 30-JUN-15:20 | 14-JUN-15:00 | 20-JUN-15:00
BLD10PST |  |  | Jul | 05-JUL-11:00 | 31-JUL-13:00 | 19-JUL-17:19 | 03-JUL-14:00 | 10-JUL-14:00 | 25-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-11:00 | 18-JUL-13:00 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-14:00 | 21-JUL-15:00
BLD10PST |  |  | Aug | 21-AUG-12:00 | 31-AUG-13:00 | 01-AUG-17:10 | 17-AUG-14:00 | 08-AUG-09:00 | 04-AUG-14:00 | 15-AUG-11:00 | 04-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 03-AUG-13:00 | 30-AUG-13:00 | 10-AUG-11:00 | 09-AUG-15:00 | 14-AUG-13:00 | 15-AUG-13:00
BLD10PST |  |  | Sep | 26-SEP-11:00 | 19-SEP-15:09 | 25-SEP-15:00 | 14-SEP-15:00 | 25-SEP-11:00 | 20-SEP-15:00 | 28-SEP-15:09 | 08-SEP-15:30 | 20-SEP-15:30 | 13-SEP-15:00 | 27-SEP-15:00 | 06-SEP-15:00 | 14-SEP-15:09 | 07-SEP-15:00 | 06-SEP-15:09 | 07-SEP-15:00
BLD10PST |  |  | Oct | 10-OCT-15:00 | 06-OCT-15:00 | 24-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:00 | 16-OCT-15:00 | 20-OCT-15:00 | 11-OCT-15:00 | 17-OCT-15:00 | 04-OCT-15:09 | 05-OCT-15:20 | 06-OCT-15:09 | 06-OCT-15:00 | 27-OCT-13:50 | 30-OCT-07:10
BLD10PST |  |  | Nov | 01-NOV-15:00 | 03-NOV-15:30 | 13-NOV-16:00 | 22-NOV-16:10 | 20-NOV-12:00 | 10-NOV-16:40 | 16-NOV-15:00 | 03-NOV-11:00 | 08-NOV-16:10 | 03-NOV-13:00 | 02-NOV-15:00 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-12:00 | 09-NOV-12:00 | 27-NOV-10:09
BLD10PST |  |  | Dec | 13-DEC-16:10 | 19-DEC-16:10 | 11-DEC-16:19 | 26-DEC-13:00 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 20-DEC-16:00 | 08-DEC-14:00 | 26-DEC-16:19 | 29-DEC-16:00 | 21-DEC-14:39 | 29-DEC-16:00 | 18-DEC-08:09 | 20-DEC-16:00 | 29-DEC-11:09
BLD10PST |  | Source Energy
BLD10PST |  |  | Total Source Energy (GJ) | 82782.4 | 72566.85 | 66216.52 | 55765.19 | 44300.97 | 59836.97 | 37119.17 | 55868.73 | 43652.91 | 24668.46 | 53688.81 | 42009.37 | 53449.11 | 44741.63 | 50139.49 | 62590.46
BLD10PST |  |  | Total Source Energy (MJ/m2) | 4225.32 | 3703.9 | 3379.77 | 2846.32 | 2261.18 | 3054.15 | 1894.61 | 2851.61 | 2228.1 | 1259.11 | 2740.34 | 2144.21 | 2728.11 | 2283.67 | 2559.18 | 3194.69
BLD10PST |  | Water Consumption (m3)
BLD10PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Water Systems | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
BLD10PST |  |  | Total Building | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
BLD10PST |  | Emissions
BLD10PST |  |  | Carbon Equivalent (kg) | 1895370 | 1823760 | 1732270 | 1370680 | 477731.3361 | 1535290 | 417953.4488 | 1133730 | 1389500 | 326678.2094 | 1959750 | 1293700 | 1315290 | 1156040 | 1191370 | 1207120
BLD10PST |  |  | CO2 (kg) | 4397450 | 4595500 | 4094370 | 3165650 | 1283320 | 3664730 | 1133070 | 2632170 | 3291630 | 845583.2727 | 4629190 | 3089090 | 3173470 | 2799170 | 2915770 | 3215870
BLD10PST |  |  | NOX (kg) | 7718.2742 | 5981.1021 | 6833.5686 | 5851.6715 | 1103.6244 | 5894.6428 | 981.462 | 4825.0905 | 5539.1646 | 1085.2027 | 7941.86 | 5093.3633 | 5150.2089 | 4477.8764 | 4552.9988 | 3530.7392
BLD10PST |  |  | SO2 (kg) | 29348.4838 | 25359.3855 | 22565.3796 | 14613.0338 | 11003.7932 | 24151.9912 | 8454.7176 | 13460.8563 | 13823.1074 | 2031.6869 | 22439.0577 | 12404.448 | 7404.9114 | 7018.1008 | 6220.7757 | 12802.4796
BLD10PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10PST |  |  | Hg (kg) | 0.1338 | 0.0715 | 0.0614 | 0.0538 | 0.0051 | 0.0456 | 0.0043 | 0.055 | 0.0544 | 0.0087 | 0.0687 | 0.0491 | 0.0554 | 0.0498 | 0.0471 | 0.0463
BLD10PST |  |  | Water for Electricity (m3) | 3632.25 | 8650.2 | 166685 | 25991.4 | 66391.9 | 120449 | 51007.4 | 837.0733 | 14372.4 | 26829.1 | 5165.09 | 12896.7 | 4865.22 | 166424 | 4086.37 | 2568.06
BLD10NEW |  | Program
BLD10NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD10NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD10NEW |  |  | Weighting Factor | 10.0524 | 95.5362 | 14.4042 | 118.7841 |  | 51.3966 | 6.8698 | 126.3091 | 3.9685 | 15.2202 | 143.1615 | 27.465 | 26.0558 | 5.3932 | 4.7269 | 0.77492
BLD10NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD10NEW |  |  | Exterior walls
BLD10NEW | TypeWall |  | Construction Type | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed | Steel-Framed
BLD10NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
BLD10NEW |  |  | Roof
BLD10NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD10NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD10NEW |  |  | Window
BLD10NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD10NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD10NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD10NEW |  |  | Skylights/TDD
BLD10NEW |  |  | U-Factor (W / m2·K) | 5.765 | 5.765 | 5.765 | 2.627 | 2.627 | 2.627 | 5.679 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.674 | 2.561
BLD10NEW |  |  | SHGC | 0.174 | 0.174 | 0.174 | 0.229 | 0.229 | 0.229 | 0.394 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.414 | 0.777 | 0.767
BLD10NEW |  |  | Visible transmittance | 0.029 | 0.029 | 0.029 | 0.008 | 0.008 | 0.008 | 0.09 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.855 | 0.855
BLD10NEW |  |  | Foundation
BLD10NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD10NEW |  |  | Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
BLD10NEW |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD10NEW |  | HVAC
BLD10NEW |  |  | HVAC Sizing
BLD10NEW | HVAC |  | Air Conditioning (kW) | 2366.4351 | 2376.4979 | 2198.1583 | 2186.7101 | 1739.3277 | 1875.8505 | 1706.96 | 2254.945 | 1536.8229 | 1510.2075 | 2217.7102 | 1499.5154 | 2136.6229 | 1286.0534 | 1926.1349 | 1058.063
BLD10NEW |  |  | COOLSYS1 CHILLER | 1433.9134 | 1438.5933 | 1255.5248 | 1253.2162 | 829.3954 | 950.878 | 999.2912 | 1313.718 | 707.6784 | 725.0307 | 1282.3329 | 677.4345 | 1203.1122 | 584.8858 | 978.5211 | 458.3334
BLD10NEW |  |  | PSZ-AC_1:5_COOLC DXCOIL | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 490.6879 | 360.1228 | 490.6879 | 450.0072 | 431.3644 | 490.6879 | 453.2368 | 490.6879 | 382.7021 | 490.6879 | 327.0982
BLD10NEW |  |  | PSZ-AC_2:6_COOLC DXCOIL | 119.535 | 125.12 | 131.1385 | 121.2674 | 99.4057 | 115.1091 | 96.1142 | 128.9025 | 108.9913 | 93.3151 | 123.3013 | 103.4424 | 121.2863 | 88.9406 | 135.9543 | 62.0385
BLD10NEW |  |  | PSZ-AC_3:7_COOLC DXCOIL | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 196.2751 | 145.2494 | 196.2751 | 155.4081 | 153.7999 | 196.2751 | 150.1517 | 196.2751 | 130.8393 | 196.2751 | 130.8393
BLD10NEW |  |  | PSZ-AC_4:8_COOLC DXCOIL | 14.546 | 14.3439 | 13.0542 | 13.7858 | 12.0859 | 11.4227 | 20.0203 | 13.8838 | 12.5022 | 9.8717 | 13.6353 | 12.2806 | 13.7837 | 10.2448 | 13.2188 | 5.4413
BLD10NEW |  |  | PSZ-AC_5:9_COOLC DXCOIL | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 111.4777 | 86.162 | 111.4777 | 102.2356 | 96.8256 | 111.4777 | 102.9694 | 111.4777 | 88.4408 | 111.4777 | 74.3123
BLD10NEW | HEAT |  | Heating (kW) | 2044.9665 | 2673.103 | 2332.4303 | 2804.2449 | 1999.2278 | 2390.7851 | 2648.024 | 3145.4754 | 2513.1179 | 2681.3805 | 3598.1434 | 2905.4783 | 3857.8248 | 3487.6808 | 3950.8641 | 4572.8564
BLD10NEW |  |  | HEATSYS1 BOILER | 607.8453 | 779.1028 | 727.7958 | 769.0858 | 528.1856 | 676.9445 | 967.6964 | 874.7364 | 708.0175 | 738.8774 | 957.3471 | 764.9544 | 1007.6678 | 898.62 | 1023.5416 | 1014.542
BLD10NEW |  |  | PSZ-AC_1:5_HEATC | 765.0269 | 1009.9404 | 852.0818 | 1089.4655 | 795.6607 | 921.1228 | 879.4681 | 1212.7703 | 963.6127 | 1048.8159 | 1416.7661 | 1150.2765 | 1531.1076 | 1395.2101 | 1567.2052 | 1940.738
BLD10NEW |  |  | PSZ-AC_2:6_HEATC | 169.6012 | 221.1158 | 195.4696 | 231.787 | 156.7562 | 193.5592 | 203.5508 | 263.0206 | 210.6753 | 212.2395 | 296.0842 | 238.077 | 315.7493 | 282.3318 | 334.9677 | 368.0869
BLD10NEW |  |  | PSZ-AC_3:7_HEATC | 306.0108 | 403.9762 | 340.8327 | 435.7862 | 318.2643 | 368.4491 | 351.7872 | 485.1081 | 385.4451 | 419.5263 | 566.7064 | 460.1106 | 612.443 | 558.084 | 626.8821 | 776.2952
BLD10NEW |  |  | PSZ-AC_4:8_HEATC | 22.6785 | 29.5229 | 22.6687 | 30.6083 | 19.5976 | 21.4428 | 45.718 | 34.3147 | 26.4474 | 23.6444 | 39.3692 | 30.7322 | 43.0098 | 36.4618 | 42.2194 | 32.2845
BLD10NEW |  |  | PSZ-AC_5:9_HEATC | 173.8039 | 229.445 | 193.5816 | 247.512 | 180.7635 | 209.2668 | 199.8034 | 275.5253 | 218.92 | 238.277 | 321.8704 | 261.3275 | 347.8472 | 316.9731 | 356.0481 | 440.9098
BLD10NEW |  |  | HVAC Efficiency
BLD10NEW | COP |  | Air Conditioning (COP) | 2.9514 | 2.9517 | 2.9647 | 2.9639 | 2.9998 | 2.9886 | 2.9603 | 2.9604 | 3.0063 | 2.9979 | 2.9619 | 3.0091 | 2.9677 | 3.0082 | 2.9891 | 3.0192
BLD10NEW |  |  | COOLSYS1 CHILLER | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
BLD10NEW |  |  | PSZ-AC_1:5_COOLC DXCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD10NEW |  |  | PSZ-AC_2:6_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3
BLD10NEW |  |  | PSZ-AC_3:7_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD10NEW |  |  | PSZ-AC_4:8_COOLC DXCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD10NEW |  |  | PSZ-AC_5:9_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
BLD10NEW | EffHeat |  | Heating Efficiency (%) | 0.7713 | 0.78022 | 0.77083 | 0.78022 | 0.77227 | 0.77168 | 0.78035 | 0.78022 | 0.77176 | 0.78018 | 0.78022 | 0.78021 | 0.78022 | 0.78021 | 0.78021 | 0.78014
BLD10NEW |  |  | HEATSYS1 BOILER | 0.75 | 0.78 | 0.75 | 0.78 | 0.75 | 0.75 | 0.78 | 0.78 | 0.75 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10NEW |  |  | PSZ-AC_1:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10NEW |  |  | PSZ-AC_2:6_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10NEW |  |  | PSZ-AC_3:7_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10NEW |  |  | PSZ-AC_4:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD10NEW |  |  | PSZ-AC_5:9_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD10NEW |  |  | HVAC Control - Economizer
BLD10NEW |  |  | PSZ-AC_1:5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10NEW |  |  | PSZ-AC_2:6_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10NEW |  |  | PSZ-AC_3:7_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10NEW |  |  | PSZ-AC_4:8_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD10NEW |  |  | PSZ-AC_5:9_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10NEW |  |  | VAV_OTHER_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10NEW |  |  | VAV_POD_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10NEW |  |  | VAV_POD_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10NEW |  |  | VAV_POD_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD10NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 79.44 | 80.99 | 84.3 | 78.14 | 72.39 | 78.41 | 97.67 | 79.78 | 80.17 | 76.97 | 78.04 | 76.76 | 77.28 | 75.81 | 77.58 | 68.32
BLD10NEW |  |  | BATHROOMS_ZN_1_FLR_1 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BLD10NEW |  |  | BATHROOMS_ZN_1_FLR_2 EXHAUST FAN | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
BLD10NEW |  |  | CAFETERIA_ZN_1_FLR_1 EXHAUST FAN | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63 | 1.63
BLD10NEW |  |  | KITCHEN_ZN_1_FLR_1 EXHAUST FAN | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
BLD10NEW |  |  | PSZ-AC_1:5_FAN | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76 | 19.76
BLD10NEW |  |  | PSZ-AC_2:6_FAN | 4.81 | 5.04 | 5.28 | 4.88 | 4 | 4.64 | 5.35 | 5.19 | 5.22 | 4.34 | 4.97 | 4.8 | 4.88 | 4.64 | 5.47 | 3.75
BLD10NEW |  |  | PSZ-AC_3:7_FAN | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9
BLD10NEW |  |  | PSZ-AC_4:8_FAN | 0.59 | 0.58 | 0.53 | 0.56 | 0.49 | 0.46 | 1.03 | 0.56 | 0.54 | 0.45 | 0.55 | 0.53 | 0.56 | 0.52 | 0.53 | 0.33
BLD10NEW |  |  | PSZ-AC_5:9_FAN | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49 | 4.49
BLD10NEW |  |  | VAV_OTHER_FAN | 13.43 | 13.88 | 14.57 | 13.04 | 11.2 | 12.76 | 16.15 | 13.29 | 13.24 | 11.74 | 12.66 | 12.12 | 12.39 | 11.78 | 12.02 | 10.49
BLD10NEW |  |  | VAV_POD_1_FAN | 8.56 | 8.87 | 9.67 | 8.24 | 7.26 | 8.53 | 13.74 | 8.62 | 8.73 | 8.55 | 8.31 | 8.11 | 8.17 | 7.97 | 8.25 | 6.25
BLD10NEW |  |  | VAV_POD_2_FAN | 8.4 | 8.68 | 9.48 | 8.07 | 7.1 | 8.36 | 13.34 | 8.43 | 8.52 | 8.31 | 8.14 | 7.9 | 8 | 7.77 | 8 | 6.21
BLD10NEW |  |  | VAV_POD_3_FAN | 9.01 | 9.3 | 10.13 | 8.71 | 7.7 | 9.02 | 13.42 | 9.05 | 9.28 | 8.94 | 8.77 | 8.66 | 8.64 | 8.49 | 8.67 | 6.65
BLD10NEW |  | Utility Costs
BLD10NEW |  |  | Electric Utility Rates
BLD10NEW |  |  | Average Annual Rate ($/kWh) | 0.081268 | 0.11226 | 0.078691 | 0.10076 | 0.060437 | 0.098504 | 0.16639 | 0.080537 | 0.036995 | 0.074524 | 0.083162 | 0.037002 | 0.065486 | 0.079761 | 0.064712 | 0.096882
BLD10NEW |  |  | Total Cost ($/m2) | 22.34 | 26.11 | 19.26 | 18.35 | 9.14 | 18.94 | 21.87 | 13.53 | 5.42 | 8.87 | 12.66 | 4.88 | 9.46 | 9.64 | 7.9 | 10.71
BLD10NEW |  |  | Gas Utility Rates
BLD10NEW |  |  | Average Annual Rate ($/MJ) | 0.011429 | 0.0080806 | 0.0082902 | 0.0097412 | 0.0085464 | 0.0077548 | 0.0085645 | 0.0097024 | 0.006926 | 0.0084062 | 0.0083637 | 0.0069455 | 0.0078692 | 0.0081481 | 0.0078681 | 0.004134
BLD10NEW |  |  | Total Cost ($/m2) | 0.44 | 1.02 | 0.82 | 2.06 | 0.71 | 1.03 | 1.69 | 3.41 | 1.68 | 2.81 | 3.84 | 2.37 | 4.85 | 4.09 | 5.82 | 4.75
BLD10NEW |  |  | Total Utility Costs
BLD10NEW |  |  | Cost Intensity ($/m2) | 22.79 | 27.13 | 20.08 | 20.41 | 9.85 | 19.97 | 23.56 | 16.94 | 7.1 | 11.68 | 16.49 | 7.25 | 14.31 | 13.73 | 13.72 | 15.46
BLD10NEW |  | Energy - End Uses
BLD10NEW |  |  | Electricity (kWh)
BLD10NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Cooling | 3335219.4444 | 2531572.2222 | 2746291.6667 | 1566727.7778 | 979636.1111 | 1745805.5556 | 590897.2222 | 1290913.8889 | 854138.8889 | 364144.4444 | 982752.7778 | 588622.2222 | 828616.6667 | 369127.7778 | 374913.8889 | 135544.4444
BLD10NEW |  |  | Interior Lighting | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333 | 939483.3333
BLD10NEW |  |  | Exterior Lighting | 78358.3333 | 78327.7778 | 78313.8889 | 78302.7778 | 78241.6667 | 78225 | 78266.6667 | 78219.4444 | 78247.2222 | 78091.6667 | 78230.5556 | 78186.1111 | 78180.5556 | 78161.1111 | 78116.6667 | 77638.8889
BLD10NEW |  |  | Interior Equipment | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778 | 632727.7778
BLD10NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Fans | 339963.8889 | 320611.1111 | 344511.1111 | 303747.2222 | 287508.3333 | 321663.8889 | 291872.2222 | 304355.5556 | 318238.8889 | 277119.4444 | 304933.3333 | 303377.7778 | 307519.4444 | 306183.3333 | 325377.7778 | 339816.6667
BLD10NEW |  |  | Pumps | 16827.7778 | 12161.1111 | 12336.1111 | 8005.5556 | 5944.4444 | 9088.8889 | 3477.7778 | 6616.6667 | 6158.3333 | 2847.2222 | 5466.6667 | 4705.5556 | 5586.1111 | 4291.6667 | 4844.4444 | 5850
BLD10NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Refrigeration | 43672.2222 | 41769.4444 | 41911.1111 | 40013.8889 | 40047.2222 | 40658.3333 | 38377.7778 | 38847.2222 | 38866.6667 | 37638.8889 | 38041.6667 | 37852.7778 | 37622.2222 | 36991.6667 | 36425 | 35547.2222
BLD10NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total End Uses | 5386258.3333 | 4556655.5556 | 4795577.7778 | 3569008.3333 | 2963591.6667 | 3767652.7778 | 2575102.7778 | 3291161.1111 | 2867863.8889 | 2332055.5556 | 2981636.1111 | 2584958.3333 | 2829736.1111 | 2366966.6667 | 2391886.1111 | 2166605.5556
BLD10NEW |  |  | Gas (MJ)
BLD10NEW |  |  | Heating | 154840 | 1791180 | 1283790 | 3401220 | 914390 | 1912860 | 3101940 | 6115510 | 3992340 | 5743450 | 8172930 | 5861040 | 11219000 | 8984290 | 13581750 | 21521580
BLD10NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Equipment | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390 | 353390
BLD10NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems | 253290 | 319760 | 289380 | 378840 | 358800 | 332800 | 408800 | 425840 | 416770 | 442430 | 465820 | 462090 | 501500 | 504770 | 554740 | 617760
BLD10NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total End Uses | 761520 | 2464340 | 1926570 | 4133440 | 1626580 | 2599050 | 3864140 | 6894750 | 4762500 | 6539270 | 8992150 | 6676530 | 12073890 | 9842450 | 14489880 | 22492740
BLD10NEW |  |  | Purchased Cooling (MJ)
BLD10NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Purchased Heating (MJ)
BLD10NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total Building (MJ) | 20152040 | 18868300 | 19190650 | 16981880 | 12295510 | 16162600 | 13134510 | 18742930 | 15086820 | 14934670 | 19726040 | 15982370 | 22260940 | 18363530 | 23100670 | 30292520
BLD10NEW |  | Energy - End Use Intensities
BLD10NEW |  |  | Electricity (MJ/m2)
BLD10NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Cooling (elec) | 612.8415 | 465.1725 | 504.6269 | 287.8838 | 180.0066 | 320.7891 | 108.5765 | 237.2035 | 156.9467 | 66.911 | 180.5793 | 108.1584 | 152.257 | 67.8267 | 68.8899 | 24.9061
BLD10NEW |  |  | Interior Lighting (elec) | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286 | 172.6286
BLD10NEW |  |  | Exterior Lighting (elec) | 14.3982 | 14.3926 | 14.3901 | 14.388 | 14.3768 | 14.3737 | 14.3814 | 14.3727 | 14.3778 | 14.3492 | 14.3747 | 14.3666 | 14.3656 | 14.362 | 14.3538 | 14.266
BLD10NEW |  |  | Interior Equipment (elec) | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628 | 116.2628
BLD10NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Fans (elec) | 62.4678 | 58.9118 | 63.3034 | 55.8131 | 52.8292 | 59.1052 | 53.6311 | 55.9249 | 58.4759 | 50.9203 | 56.031 | 55.7452 | 56.5062 | 56.2607 | 59.7877 | 62.4408
BLD10NEW |  |  | Pumps (elec) | 3.0921 | 2.2346 | 2.2667 | 1.471 | 1.0923 | 1.6701 | 0.63904 | 1.2158 | 1.1316 | 0.52317 | 1.0045 | 0.86464 | 1.0264 | 0.78859 | 0.89016 | 1.0749
BLD10NEW |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Refrigeration (elec) | 8.0247 | 7.6751 | 7.7011 | 7.3525 | 7.3586 | 7.4709 | 7.0519 | 7.1381 | 7.1417 | 6.9161 | 6.9901 | 6.9554 | 6.913 | 6.7972 | 6.693 | 6.5317
BLD10NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total End Uses | 989.7167 | 837.2785 | 881.1801 | 655.7998 | 544.5554 | 692.3004 | 473.1712 | 604.7458 | 526.9656 | 428.5116 | 547.8711 | 474.9821 | 519.9597 | 434.9265 | 439.5054 | 398.1105
BLD10NEW |  |  | Gas (MJ/m2)
BLD10NEW |  |  | Heating (gas) | 7.9032 | 91.4241 | 65.5262 | 173.6025 | 46.6716 | 97.6347 | 158.3269 | 312.1432 | 203.774 | 293.1528 | 417.1565 | 299.1548 | 572.6317 | 458.5693 | 693.2294 | 1098.4882
BLD10NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Equipment (gas) | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375 | 18.0375
BLD10NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems (gas) | 12.9282 | 16.3209 | 14.7703 | 19.3365 | 18.3136 | 16.9865 | 20.8657 | 21.7354 | 21.2725 | 22.5822 | 23.776 | 23.5856 | 25.5972 | 25.7641 | 28.3146 | 31.5312
BLD10NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total End Uses | 38.8689 | 125.783 | 98.3345 | 210.9759 | 83.0227 | 132.6587 | 197.2305 | 351.9166 | 243.0839 | 333.7725 | 458.9705 | 340.7784 | 616.2663 | 502.3709 | 739.5815 | 1148.0574
BLD10NEW |  |  | Purchased Cooling (MJ/m2)
BLD10NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Purchased Heating (MJ/m2)
BLD10NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Total Building (MJ/m2) | 1028.5851 | 963.0615 | 979.5146 | 866.7762 | 627.5781 | 824.9592 | 670.4017 | 956.6624 | 770.05 | 762.2841 | 1006.8416 | 815.76 | 1136.226 | 937.2974 | 1179.0869 | 1546.1678
BLD10NEW |  | Peak Energy Demand
BLD10NEW |  |  | Electricity Peak Demand (kW)
BLD10NEW |  |  | Jan | 1196.6515 | 1190.8535 | 1098.6752 | 880.1278 | 913.5609 | 867.9179 | 652.7774 | 595.1012 | 690.4612 | 450.2359 | 452.9999 | 745.4716 | 454.9307 | 464.9267 | 456.4077 | 471.2785
BLD10NEW |  |  | Feb | 1217.9073 | 1260.8113 | 1146.7287 | 828.0171 | 894.4 | 908.8317 | 918.5783 | 606.0902 | 792.534 | 675.0251 | 452.8105 | 625.1294 | 452.8091 | 694.3327 | 455.9076 | 463.0906
BLD10NEW |  |  | Mar | 1262.6745 | 1210.7664 | 1240.5408 | 1101.741 | 885.9792 | 967.5682 | 857.365 | 1144.5196 | 794.5117 | 784.2963 | 1062.4393 | 808.1113 | 698.1228 | 734.2483 | 453.3099 | 462.7844
BLD10NEW |  |  | Apr | 1259.5127 | 1264.9213 | 1264.7352 | 1163.7761 | 959.5068 | 1093.4868 | 927.9895 | 1139.8418 | 890.9621 | 754.6744 | 1060.3708 | 830.2067 | 1040.99 | 722.2949 | 747.8667 | 449.599
BLD10NEW |  |  | May | 1296.5882 | 1308.972 | 1327.2771 | 1187.9909 | 882.4387 | 1158.2597 | 957.0466 | 1170.8406 | 951.2474 | 841.1231 | 1205.758 | 902.1131 | 1143.5878 | 790.2447 | 964.8803 | 656.5695
BLD10NEW |  |  | Jun | 1320.5413 | 1327.0683 | 1424.9517 | 1241.0952 | 890.4714 | 1237.6354 | 977.2861 | 1283.9562 | 998.278 | 857.7249 | 1243.5191 | 970.9076 | 1215.823 | 921.3838 | 1050.3369 | 731.1299
BLD10NEW |  |  | Jul | 1143.0705 | 1186.0901 | 1258.8639 | 1091.2982 | 739.3374 | 1064.8193 | 865.3489 | 1106.8018 | 838.1785 | 726.295 | 1091.3565 | 812.8598 | 1007.9144 | 726.4821 | 888.9637 | 545.8645
BLD10NEW |  |  | Aug | 1139.1765 | 1183.6636 | 1282.707 | 1048.888 | 787.2828 | 1057.9464 | 852.194 | 1114.3515 | 813.7445 | 698.3858 | 1044.9299 | 809.5195 | 982.3837 | 685.4296 | 850.1812 | 541.397
BLD10NEW |  |  | Sep | 1292.5365 | 1304.774 | 1357.0134 | 1194.4498 | 990.6357 | 1157.6406 | 1060.1692 | 1272.6614 | 927.2149 | 879.0487 | 1237.3536 | 931.8963 | 1132.8918 | 814.1025 | 966.4662 | 607.2361
BLD10NEW |  |  | Oct | 1265.2693 | 1303.9644 | 1264.1846 | 1224.4137 | 965.1734 | 1093.9881 | 955.7376 | 1206.7839 | 871.607 | 792.9984 | 1127.4275 | 883.7914 | 1050.2676 | 756.2462 | 870.8227 | 459.8995
BLD10NEW |  |  | Nov | 1234.9421 | 1220.2158 | 1199.9593 | 1043.1432 | 913.9091 | 920.6435 | 853.3197 | 1086.2077 | 774.4953 | 634.9045 | 1088.8522 | 765.2465 | 909.772 | 529.2884 | 465.294 | 465.8995
BLD10NEW |  |  | Dec | 1218.8637 | 1201.9119 | 1090.0416 | 881.4813 | 920.5901 | 900.648 | 671.5494 | 453.8095 | 621.5799 | 450.244 | 451.6682 | 568.9522 | 452.0821 | 463.8941 | 453.7355 | 470.8295
BLD10NEW |  |  | Time of Peak Electrical Demand
BLD10NEW |  |  | Jan | 06-JAN-12:00 | 02-JAN-16:19 | 26-JAN-16:10 | 23-JAN-15:00 | 26-JAN-12:00 | 18-JAN-14:00 | 17-JAN-14:00 | 09-JAN-11:00 | 26-JAN-15:00 | 27-JAN-11:39 | 27-JAN-11:09 | 27-JAN-12:00 | 05-JAN-11:09 | 05-JAN-08:09 | 09-JAN-11:09 | 02-JAN-11:09
BLD10NEW |  |  | Feb | 22-FEB-16:10 | 23-FEB-16:10 | 28-FEB-16:00 | 17-FEB-14:00 | 13-FEB-11:00 | 08-FEB-16:10 | 15-FEB-16:10 | 15-FEB-15:00 | 14-FEB-16:10 | 21-FEB-13:00 | 17-FEB-11:39 | 07-FEB-14:00 | 03-FEB-11:09 | 02-FEB-14:00 | 01-FEB-11:09 | 03-FEB-08:20
BLD10NEW |  |  | Mar | 13-MAR-15:00 | 27-MAR-15:09 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-10:50 | 31-MAR-15:00 | 20-MAR-14:00 | 09-MAR-16:10 | 02-MAR-16:10 | 29-MAR-15:00 | 31-MAR-14:00 | 30-MAR-15:00 | 23-MAR-14:00 | 30-MAR-15:00 | 01-MAR-11:39 | 14-MAR-07:19
BLD10NEW |  |  | Apr | 03-APR-15:20 | 28-APR-15:30 | 26-APR-15:39 | 14-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 13-APR-15:09 | 04-APR-15:00 | 21-APR-15:00 | 18-APR-13:00 | 07-APR-14:39 | 25-APR-15:09 | 14-APR-15:00 | 06-APR-15:00 | 04-APR-14:00 | 26-APR-10:39
BLD10NEW |  |  | May | 24-MAY-14:00 | 26-MAY-14:00 | 30-MAY-15:00 | 12-MAY-15:00 | 30-MAY-09:09 | 31-MAY-15:00 | 09-MAY-11:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 04-MAY-15:00 | 23-MAY-15:00 | 15-MAY-15:20 | 16-MAY-15:00 | 31-MAY-15:00 | 24-MAY-15:20
BLD10NEW |  |  | Jun | 09-JUN-15:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-15:30 | 30-JUN-15:20 | 27-JUN-15:00 | 16-JUN-10:39 | 23-JUN-15:00 | 29-JUN-13:00 | 28-JUN-15:20 | 06-JUN-15:00 | 28-JUN-11:00 | 30-JUN-15:20 | 30-JUN-15:20 | 14-JUN-15:39 | 20-JUN-15:00
BLD10NEW |  |  | Jul | 05-JUL-11:00 | 31-JUL-13:00 | 19-JUL-17:19 | 03-JUL-14:00 | 10-JUL-14:00 | 25-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 14-JUL-11:00 | 18-JUL-13:00 | 13-JUL-14:00 | 21-JUL-15:00 | 06-JUL-14:00 | 21-JUL-15:00
BLD10NEW |  |  | Aug | 21-AUG-12:00 | 31-AUG-13:00 | 01-AUG-17:10 | 17-AUG-14:00 | 08-AUG-09:00 | 04-AUG-14:00 | 15-AUG-11:00 | 04-AUG-14:00 | 01-AUG-13:00 | 07-AUG-14:00 | 03-AUG-13:00 | 30-AUG-13:00 | 25-AUG-13:00 | 09-AUG-15:00 | 11-AUG-13:00 | 15-AUG-13:00
BLD10NEW |  |  | Sep | 26-SEP-11:00 | 19-SEP-15:09 | 25-SEP-13:00 | 14-SEP-15:00 | 25-SEP-11:00 | 20-SEP-15:00 | 28-SEP-15:09 | 08-SEP-15:20 | 20-SEP-15:20 | 13-SEP-15:00 | 27-SEP-15:00 | 06-SEP-15:00 | 14-SEP-15:09 | 07-SEP-15:00 | 07-SEP-15:09 | 07-SEP-14:00
BLD10NEW |  |  | Oct | 10-OCT-15:39 | 06-OCT-15:00 | 02-OCT-15:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:00 | 16-OCT-15:00 | 20-OCT-15:00 | 11-OCT-15:00 | 17-OCT-15:00 | 04-OCT-15:20 | 05-OCT-15:20 | 06-OCT-15:09 | 06-OCT-15:00 | 06-OCT-14:00 | 31-OCT-07:10
BLD10NEW |  |  | Nov | 01-NOV-15:00 | 03-NOV-15:20 | 13-NOV-16:00 | 22-NOV-16:10 | 20-NOV-12:00 | 10-NOV-16:40 | 16-NOV-15:00 | 03-NOV-11:00 | 08-NOV-16:10 | 03-NOV-13:00 | 02-NOV-15:20 | 10-NOV-13:00 | 02-NOV-14:00 | 21-NOV-12:00 | 09-NOV-12:00 | 27-NOV-10:09
BLD10NEW |  |  | Dec | 13-DEC-16:10 | 19-DEC-16:10 | 11-DEC-16:19 | 26-DEC-14:00 | 19-DEC-12:00 | 05-DEC-12:00 | 07-DEC-14:00 | 06-DEC-11:39 | 08-DEC-14:00 | 28-DEC-11:39 | 12-DEC-11:39 | 21-DEC-14:30 | 20-DEC-11:09 | 18-DEC-08:09 | 20-DEC-11:09 | 29-DEC-11:09
BLD10NEW |  | Source Energy
BLD10NEW |  |  | Total Source Energy (GJ) | 65149.95 | 62270.23 | 56710.1 | 47735.85 | 34796.55 | 51354.99 | 32911.43 | 49898.17 | 39456.72 | 21765.66 | 47881.81 | 38167.57 | 48197.57 | 40367.24 | 45418.24 | 52422.9
BLD10NEW |  |  | Total Source Energy (MJ/m2) | 3325.33 | 3178.35 | 2894.55 | 2436.5 | 1776.06 | 2621.22 | 1679.84 | 2546.86 | 2013.92 | 1110.95 | 2443.95 | 1948.12 | 2460.06 | 2060.39 | 2318.2 | 2675.73
BLD10NEW |  | Water Consumption (m3)
BLD10NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Water Systems | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
BLD10NEW |  |  | Total Building | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93 | 2677.93
BLD10NEW |  | Emissions
BLD10NEW |  |  | Carbon Equivalent (kg) | 1490910 | 1564360 | 1482410 | 1173920 | 375674.0988 | 1317600 | 370622.3622 | 1012470 | 1257400 | 287773.8826 | 1751810 | 1176350 | 1186320 | 1042460 | 1080020 | 1015260
BLD10NEW |  |  | CO2 (kg) | 3460160 | 3942310 | 3504850 | 2710520 | 1009420 | 3145160 | 1004780 | 2350900 | 2977870 | 744178.674 | 4136260 | 2808310 | 2862050 | 2524620 | 2642410 | 2699070
BLD10NEW |  |  | NOX (kg) | 6068.4122 | 5129.6127 | 5845.2449 | 5013.6742 | 868.2516 | 5058.7117 | 870.3571 | 4308.2959 | 5014.7154 | 957.6 | 7103.9563 | 4632.7827 | 4645.9134 | 4036.7336 | 4129.6884 | 2977.1935
BLD10NEW |  |  | SO2 (kg) | 23055.5389 | 21735.9046 | 19284.495 | 12528.33 | 8624.1282 | 20725.8039 | 7494.276 | 12015.9056 | 12524.6685 | 1804.2446 | 20096.2561 | 11289.7834 | 6681.863 | 6322.7249 | 5649.119 | 11034.9228
BLD10NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD10NEW |  |  | Hg (kg) | 0.1051 | 0.0613 | 0.0525 | 0.0461 | 0.004 | 0.0391 | 0.0038 | 0.0491 | 0.0493 | 0.0077 | 0.0615 | 0.0447 | 0.05 | 0.0449 | 0.0428 | 0.0398
BLD10NEW |  |  | Water for Electricity (m3) | 2853.41 | 7414.21 | 142450 | 22283.5 | 52034 | 103362 | 45213 | 747.2175 | 13022.4 | 23826.1 | 4625.83 | 11737.8 | 4390.16 | 149934 | 3710.87 | 2213.58

## Picture
DOE Commercial Building Benchmark - Secondary School

## Schedules
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Kitchen_Exhaust_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | 11.25 | 586.61
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchEquip1 | WD | BLDG_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69 | 3348.11
| Sat |  |  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
| Sun |  |  |  | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
SchEquip2 | WD |  |  | Through 9/1 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 8.25 | 41.25
| Sat |  |  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
| Sun |  |  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  |  | Through 12/31 | WD, SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 13.8 | 69
[5 empty] | Other | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
SchLight1 | WD | BLDG_LIGHT_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87 | 3466.2
| Sat |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
| Sun |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
SchLight2 | WD |  |  | Through 9/1 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 8.13 | 40.64
| Sat |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
| Sun |  |  |  | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
|  |  |  | Through 12/31 | WD, SummerDesign | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773 | 14.37 | 71.87
[5 empty] | Other | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 4.26
SchOcc1 | WD | BLDG_OCC_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75 | 1457.54
| Sat |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchOcc2 | WD |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 1.95 | 9.75
| Sat |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 6.35 | 31.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_OCC_SCH_Auditorium | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.95 | 19.75 | 944.32
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0 | 2.05 | 10.25
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.95 | 19.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_OCC_SCH_Cafeteria | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 13 | 628.36
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | 7.5
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.05 | 0.05 | 0.95 | 0.95 | 0.15 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6 | 13
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_OCC_SCH_Extend | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5 | 2255.5
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 6.5 | 32.5
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0 | 0 | 0 | 9.1 | 45.5
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_OCC_SCH_Gym | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75 | 1833.39
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 4.55 | 22.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 7.55 | 37.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | BLDG_OCC_SCH_Offices | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75 | 2176.29
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 22.5
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0 | 9.15 | 45.75
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | KITCHEN_ELEC_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 15.25 | 784.83
[5 empty] | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  |  |  | Through 9/1 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.13 | 0.13 | 0.2 | 0.2 | 0.2 | 0.13 | 0.13 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.82 | 14.1
[5 empty] | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
|  |  |  | Through 12/31 | WD, SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 3.05 | 15.25
[5 empty] | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 2.4
SchGas1 | WD | KITCHEN_GAS_EQUIP_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 7.2 | 389.41
| Sat |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
| Sun |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
SchGas2 | WD |  |  | Through 9/1 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.1 | 0.15 | 0.15 | 0.15 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.19 | 6.91
| Sat |  |  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
| Sun |  |  |  | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  |  |  | Through 12/31 | WD, SummerDesign | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 1.44 | 8.16
[5 empty] | WE, WinterDesign, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.48
|  | INFIL_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 17 | 119 | 6205
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8 | 7800
|  |  |  | Through 09/30 | All | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 14.4 | 100.8
|  |  |  | Through 12/31 | All | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 26.4 | 184.8
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SetCool1 | WD | CLGSETP_SCH | Temperature | Through 6/30 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296 | 67577.14
| Sat |  |  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
| Sun |  |  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603
SetCool2 | WD |  |  | Through 9/1 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
| Sat |  |  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
| Sun |  |  |  | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
[5 empty] | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 27 | 27 | 27 | 615
|  |  |  | Through 12/31 | SummerDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 1296
[5 empty] | WE, Hol, WinterDesign | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
[5 empty] | Other | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603
|  | CLGSETP_SCH_BathCorrMechKitchen | Temperature | Through 12/31 | SummerDesign | 27 | 27 | 27 | 27 | 27 | 27 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 27 | 27 | 27 | 603 | 0 | 0
[5 empty] | Other | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 648
SetHeat1 | WD | HTGSETP_SCH | Temperature | Through 6/30 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768 | 40045.71
| Sat |  |  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
| Sun |  |  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
[5 empty] | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459
SetHeat2 | WD |  |  | Through 9/1 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
| Sat |  |  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
| Sun |  |  |  | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
[5 empty] | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 16 | 16 | 16 | 439
|  |  |  | Through 12/31 | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 768
[5 empty] | WE, Hol, SummerDesign | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
[5 empty] | Other | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459
|  | HTGSETP_SCH_BathCorrMechKitchen | Temperature | Through 12/31 | WinterDesign | 16 | 16 | 16 | 16 | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 459 | 0 | 0
[5 empty] | Other | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384
|  | HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MinOA_Sched | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 75 | 3910.71
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
|  | HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1608 | 11256 | 586920
|  | PlantOnSched | Any Number | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
|  | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
|  | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
|  | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
[5 empty] | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
|  | Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
SchSWH1 | WD | BLDG_SWH_SCH | Fraction | Through 6/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19 | 1599.88
| Sat |  |  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
| Sun |  |  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
SchSWH2 | WD |  |  | Through 9/15 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 2.54 | 14.34
| Sat |  |  |  | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
| Sun |  |  |  | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  |  |  | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0.22 | 0.22 | 0.12 | 0.09 | 6.91 | 36.19
[5 empty] | Sat, WinterDesign | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.8
[5 empty] | Sun, Hol, Other | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.84
|  | Showers_SWH_SCH | Fraction | Through 6/30 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8 | 1848.37
[5 empty] | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
[5 empty] | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 9/1 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5
[5 empty] | WE, WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 7.6 | 41.8
[5 empty] | WE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 1.9
[5 empty] | WinterDesign, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | SHW_default Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Kitchen Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
|  | SHW_Kitchen Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600