## 1
1 | Building Summary Hospital
UWG |  |  | Pre80 | Post80 | New
areaFloor |  | Total Floor Area (m2) | 22422.1768 | 22422.1768 | 22422.1768
nFloor |  | Number of Floors | 5 plus basement | 5 plus basement | 5 plus basement
glazing |  | Total | 0.5 | 0.5 | 0.5
hCeiling |  | Floor to Ceiling Height (m) | 3.2 | 3.2 | 3.2
areaWall |  | Gross Dimensions - Total Area (m2) | 5184.32 | 5184.32 | 5184.32
ver2hor |  | Wall to Skin Ratio | 0.41902 | 0.41902 | 0.41902
areaRoof |  | Gross Dimensions - Total Area (m2) | 3739.134 | 3739.134 | 3739.134
areaWindow |  | Total Area (m2) | 845.42 | 845.42 | 845.42

## 2
1 |  | Zone Summary
UWG | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD2PRE | Total | Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 929.0434 | 9.9 | 14.9508 | 12.6348 | 1037.1996 | 6.7018 | 1.8 |  |  | 0.61445
BLD2PST | Total | Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 929.0434 | 9.9 | 14.9508 | 12.6348 | 1037.1996 | 6.7018 | 1.8 |  |  | 0.61445
BLD2NEW | Total | Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 929.0434 | 9.9 | 14.9508 | 12.6348 | 1037.1996 | 6.7018 | 1.8 |  |  | 0.61445
24.1347

## 3
3 | UWG | Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD2PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD2PRE | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD2PRE | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD2PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD2PRE | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD2PRE | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD2PRE | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD2PRE | HVAC |  | COOLSYS1 CHILLER | 3415.7574 | 3397.9324 | 3123.5546 | 3196.8153 | 2658.5769 | 2763.8652 | 2284.6301 | 3213.1319 | 2303.1765 | 2402.4192 | 3061.0916 | 2184.888 | 2948.6261 | 2079.523 | 2572.8197 | 2020.0632
BLD2PRE | HEAT |  | HEATSYS1 BOILER | 3494.7069 | 3682.0495 | 3665.5622 | 3703.9411 | 3375.9573 | 3602.6455 | 3348.3746 | 3807.0237 | 3350.7745 | 3580.51 | 3779.9148 | 3301.4912 | 3865.9818 | 3569.0303 | 3785.1825 | 4162.8318
BLD2PRE | COP |  | Air Conditioning (COP) | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081
BLD2PRE | EffHeat |  | Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
BLD2PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 114.14 | 115.49 | 120.79 | 117.24 | 109.28 | 120.97 | 105.33 | 113.02 | 121.84 | 109.38 | 107.36 | 113.96 | 106.18 | 109.45 | 103.22 | 98.59
BLD2PST | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD2PST | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD2PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD2PST | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD2PST | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD2PST | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD2PST | HVAC |  | COOLSYS1 CHILLER | 3317.7354 | 3272.1969 | 2992.1053 | 3052.2014 | 2637.6716 | 2600.8729 | 2214.0284 | 3052.2193 | 2185.9303 | 2281.7485 | 3019.3167 | 2147.4495 | 2905.9548 | 2050.9651 | 2569.7719 | 2078.5723
BLD2PST | HEAT |  | HEATSYS1 BOILER | 3292.1556 | 3444.169 | 3450.4642 | 3463.4962 | 3283.1835 | 3332.8226 | 3191.185 | 3572.7157 | 3158.2495 | 3404.7626 | 3749.1716 | 3265.9071 | 3832.2463 | 3556.5715 | 3840.169 | 4321.1484
BLD2PST | COP |  | Air Conditioning (COP) | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081
BLD2PST | EffHeat |  | Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
BLD2PST | Fan |  | Fan Max Flow Rate (m3/s ) | 109.36 | 108.93 | 113.52 | 109.53 | 108.33 | 111.41 | 101.71 | 104.6 | 114.4 | 102.77 | 105.04 | 111.7 | 103.83 | 107.71 | 102.97 | 101.52
BLD2NEW | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD2NEW | RvalWall |  | R-value (m2·K / W) | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
BLD2NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD2NEW | RvalRoof |  | R-value (m2·K / W) | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43 | 1.43
BLD2NEW | Uwindow |  | U-Factor (W / m2·K) | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18 | 3.18
BLD2NEW | SHGC |  | SHGC | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
BLD2NEW | HVAC |  | COOLSYS1 CHILLER | 2964.08 | 2945.3231 | 2673.5664 | 2709.2499 | 2279.0616 | 2291.3469 | 2030.5039 | 2763.9099 | 1929.6802 | 2053.7548 | 2726.1701 | 1913.698 | 2633.709 | 1850.7698 | 2336.5893 | 1812.409
BLD2NEW | HEAT |  | HEATSYS1 BOILER | 2897.0791 | 3064.559 | 2942.8831 | 3133.4104 | 2845.4191 | 2899.1659 | 3054.0461 | 3290.0611 | 2766.7324 | 3068.5765 | 3444.8015 | 2926.4657 | 3531.9221 | 3225.4349 | 3559.1337 | 3876.5121
BLD2NEW | COP |  | Air Conditioning (COP) | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081 | 2.081
BLD2NEW | EffHeat |  | Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
BLD2NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 96.91 | 97.52 | 99.55 | 94.99 | 91.72 | 95.03 | 92.67 | 94.29 | 98.97 | 91.56 | 94.11 | 97.95 | 93.63 | 95.67 | 93.72 | 87.08
2.52

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | CRITICAL_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6 | 130.2 | 6789
| Sat |  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
| Sun |  |  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
SchLight | WD | CRITICAL_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18 | 108 | 5631.43
| Sat |  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
| Sun |  |  |  | Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
SchOcc | WD | CRITICAL_OCC_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1 | 102.6 | 5349.86
| Sat |  |  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
| Sun |  |  |  | Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
SetCool | WD | CRITICAL_CLGSETP_SCH | Temperature | Through 12/31 | All | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 532.8 | 3729.6 | 194472
| Sat |  |  |  |  | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371
| Sun |  |  |  |  | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371
SetHeat | WD | CRITICAL_HTGSETP_SCH | Temperature | Through 12/31 | All | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 506.4 | 3544.8 | 184836
| Sat |  |  |  |  | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371
| Sun |  |  |  |  | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371 | 20.5371
SchGas | WD | Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 18.25 | 951.61
| Sat |  |  |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 18.25 | 951.61
| Sun |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
SchSWH | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
| Sat |  |  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
| Sun |  |  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24

## BuildingSummary
1 | Building Summary Hospital
UWG |  |  | Pre80 | Post80 | New
Program
|  | Building Name | Hospital pre-1980 construction | Hospital post-1980 construction | Hospital new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Health care, inpatient | Health care, inpatient | Health care, inpatient
Form
areaFloor |  | Total Floor Area (m2) | 22422.1768 | 22422.1768 | 22422.1768
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 1.3142 | 1.3142 | 1.3142
nFloor |  | Number of Floors | 5 plus basement | 5 plus basement | 5 plus basement
Window Fraction (Window to Wall Ratio)
|  | South | 0.1334 | 0.1334 | 0.1334
|  | East | 0.121 | 0.121 | 0.121
|  | North | 0.117 | 0.117 | 0.117
|  | West | 0.2315 | 0.2315 | 0.2315
glazing |  | Total | 0.1461 | 0.1461 | 0.1461
|  | Skylight/TDD Percentage | 0 | 0 | 0
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | See pictures and zone summary | See pictures and zone summary | See pictures and zone summary
hCeiling |  | Floor to Ceiling Height (m) | 4.27 | 4.27 | 4.27
|  | Floor to Floor Height (m) | 4.27 | 4.27 | 4.27
|  | Roof type | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Mass wall | Mass wall | Mass wall
areaWall |  | Gross Dimensions - Total Area (m2) | 5184.32 | 5184.32 | 5184.32
|  | Net Dimensions - Total Area (m2) | 4338.78 | 4338.78 | 4338.78
ver2hor |  | Wall to Skin Ratio | 0.41902 | 0.41902 | 0.41902
Roof
|  | Construction Type | IEAD | IEAD | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 3739.134 | 3739.134 | 3739.134
|  | Net Dimensions - Total Area (m2) | 3739.134 | 3739.134 | 3739.134
|  | Roof to Skin Ratio | 0.58098 | 0.58098 | 0.58098
Window Dimensions (m2)
|  | South | 220.72 | 220.72 | 220.72
|  | East | 144.86 | 144.86 | 144.86
|  | North | 186.18 | 186.18 | 186.18
|  | West | 293.66 | 293.66 | 293.66
areaWindow |  | Total Area (m2) | 845.42 | 845.42 | 845.42
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) | 0 | 0 | 0
|  | Operable area (m2) | 0 | 0 | 0
Foundation
|  | Foundation Type | Basement | Basement | Basement
|  | Construction | 4 in slab | 4 in slab | 4 in slab
|  | Dimensions - Total Area (m2) | 3739.134 | 3739.134 | 3739.134
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 15534.17 | 15534.17 | 15534.17
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 44872.35 | 44872.35 | 44872.35
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 0.26534 | 0.26534 | 0.070757
HVAC
|  | System Type | MZ-VAV | MZ-VAV | MZ-VAV
|  | Heating Type | Boiler | Boiler | Boiler
|  | Cooling Type | Chiller, water cooled | Chiller, water cooled | Chiller, water cooled
|  | Fan Control | CAV, VAV | CAV, VAV | CAV, VAV
Service Water Heating
|  | SWH Type | gas water heater | gas water heater | gas water heater
|  | Fuel | gas | gas | gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 4037.61 | 4037.61 | 4037.61

## ZoneSummary
1 |  | Zone Summary
UWG | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD2PRE |  | Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 19.375 | 8.0729 |  |  | 10 |  | 1006.2497 |  | 0
BLD2PRE |  | ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
BLD2PRE |  | ER_Trauma1_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PRE |  | ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.66938
BLD2PRE |  | ER_Trauma2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PRE |  | ER_Triage_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
BLD2PRE |  | Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1.0503 | 25.7922 | 11.8403 |  |  | 10 |  | 10.5034 |  | 0.89241
BLD2PRE |  | Lobby_Records_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.7804 | 62.6301 | 13.0064 | 113.3908 | 15.7328 | 1.0764 |  |  | 10 |  | 1133.9077 |  | 0.26568
BLD2PRE |  | Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  |  | 0.25 | 1349.325 |  | 0.15304 | 142.2575
BLD2PRE |  | ER_NurseStn_Lobby_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.5801 | 30.42 | 14.8645 | 83.1249 | 17.8959 | 14.6389 |  |  |  |  | 2929.9675 |  | 0.085575
BLD2PRE |  | OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.0501 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 1.1159
BLD2PRE |  | OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.44637
BLD2PRE |  | OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.66955
BLD2PRE |  | OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 84.9091 | 53.8195 |  | 7.5708 |  |  | 793.0838 |  | 0
BLD2PRE |  | IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
BLD2PRE |  | IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 41.3698 | 32.2917 |  |  |  |  | 66.0874 |  | 1.5621
BLD2PRE |  | IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
BLD2PRE |  | ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.6802 | 25.03 | 4.6452 | 133.0332 | 41.3698 | 32.2917 |  |  |  |  | 1465.3513 |  | 0.33219
BLD2PRE |  | ICU_NurseStn_Lobby_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 18.4588 | 21.5278 |  |  | 10 |  | 1585.8356 |  | 0
BLD2PRE |  | Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  | 10 | 0.25 | 1349.325 |  | 0.15304 | 142.2575
BLD2PRE |  | OR_NurseStn_Lobby_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.1402 | 35.76 | 13.0064 | 77.8568 | 15.6644 | 11.1945 |  |  | 10 |  | 2401.245 |  | 0.17199
BLD2PRE |  | PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
BLD2PRE |  | PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
BLD2PRE |  | PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
BLD2PRE |  | PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
BLD2PRE |  | PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
BLD2PRE |  | PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 26.9378 | 16.1458 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
BLD2PRE |  | PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PRE |  | PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
BLD2PRE |  | PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PRE |  | NurseStn_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
BLD2PRE |  | Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
BLD2PRE |  | Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823 | 141.6775
BLD2PRE |  | Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823 | 141.6775
BLD2PRE |  | PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
BLD2PRE |  | PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
BLD2PRE |  | PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
BLD2PRE |  | PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
BLD2PRE |  | PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
BLD2PRE |  | Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 23.8269 | 107.639 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
BLD2PRE |  | PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PRE |  | PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
BLD2PRE |  | PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PRE |  | NurseStn_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
BLD2PRE |  | Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
BLD2PRE |  | Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823 | 141.6775
BLD2PRE |  | Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823 | 141.6775
BLD2PRE |  | Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.6702 | 35.76 | 9.2903 | 74.9999 | 27.7331 | 10.7639 |  |  | 10 |  | 749.9993 |  | 0.31244
BLD2PRE |  | NurseStn_Lobby_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.0801 | 0 | 13.0064 | 79.9999 | 15.6443 | 11.1945 |  |  | 10 |  | 2467.3419 |  | 0.095647
BLD2PRE |  | Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2002 | 0 | 18.5806 | 49.9999 | 15.2932 | 80.7294 | 304.9413 | 567.81 | 15 |  | 2202.9829 | 2501.3191 | 0.26781
BLD2PRE |  | Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.5601 | 17.98 | 13.2719 | 5.2517 | 25.7922 | 10.7639 |  |  | 10 |  | 52.5171 |  | 0.98173
BLD2PRE |  | Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.44627
BLD2PRE |  | Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.5501 | 17.98 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.98187
BLD2PRE |  | Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1 | 25.7922 | 10.7639 |  |  | 10 |  | 10 |  | 0.89241
BLD2PRE |  | Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.0601 | 0 | 92.9031 | 5.4 | 14.6034 | 0 |  |  |  | 0.25 | 125.42 |  | 0.14878 | 125.42
BLD2PRE | Total | Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 1291.1824 | 21.9082 | 17.4152 | 12.6348 | 1037.1996 | 6.7018 | 1.8146 | 40687.9102 | 31.5121 | 0.22109 | 976.645
BLD2PST |  | Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 19.375 | 8.0729 |  |  | 10 |  | 1006.2497 |  | 0
BLD2PST |  | ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
BLD2PST |  | ER_Trauma1_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PST |  | ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.66938
BLD2PST |  | ER_Trauma2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PST |  | ER_Triage_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
BLD2PST |  | Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1.0503 | 25.7922 | 11.8403 |  |  | 10 |  | 10.5034 |  | 0.89241
BLD2PST |  | Lobby_Records_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.7804 | 62.6301 | 13.0064 | 113.3908 | 15.7328 | 1.0764 |  |  | 10 |  | 1133.9077 |  | 0.26568
BLD2PST |  | Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  |  | 0.25 | 1349.325 |  | 0.15304
BLD2PST |  | ER_NurseStn_Lobby_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.5801 | 30.42 | 14.8645 | 83.1249 | 17.8959 | 14.6389 |  |  |  |  | 2929.9675 |  | 0.085575
BLD2PST |  | OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.0501 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 1.1159
BLD2PST |  | OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.44637
BLD2PST |  | OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.66955
BLD2PST |  | OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 84.9091 | 53.8195 |  | 7.5708 |  |  | 793.0838 |  | 0
BLD2PST |  | IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
BLD2PST |  | IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 41.3698 | 32.2917 |  |  |  |  | 66.0874 |  | 1.5621
BLD2PST |  | IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
BLD2PST |  | ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.6802 | 25.03 | 4.6452 | 133.0332 | 41.3698 | 32.2917 |  |  |  |  | 1465.3513 |  | 0.33219
BLD2PST |  | ICU_NurseStn_Lobby_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 18.4588 | 21.5278 |  |  | 10 |  | 1585.8356 |  | 0
BLD2PST |  | Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  | 10 | 0.25 | 1349.325 |  | 0.15304
BLD2PST |  | OR_NurseStn_Lobby_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.1402 | 35.76 | 13.0064 | 77.8568 | 15.6644 | 11.1945 |  |  | 10 |  | 2401.245 |  | 0.17199
BLD2PST |  | PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
BLD2PST |  | PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
BLD2PST |  | PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
BLD2PST |  | PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
BLD2PST |  | PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
BLD2PST |  | PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 26.9378 | 16.1458 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
BLD2PST |  | PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PST |  | PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
BLD2PST |  | PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PST |  | NurseStn_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
BLD2PST |  | Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
BLD2PST |  | Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
BLD2PST |  | Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
BLD2PST |  | PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
BLD2PST |  | PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
BLD2PST |  | PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
BLD2PST |  | PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
BLD2PST |  | PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
BLD2PST |  | Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 23.8269 | 107.639 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
BLD2PST |  | PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PST |  | PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
BLD2PST |  | PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
BLD2PST |  | NurseStn_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
BLD2PST |  | Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
BLD2PST |  | Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
BLD2PST |  | Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
BLD2PST |  | Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.6702 | 35.76 | 9.2903 | 74.9999 | 27.7331 | 10.7639 |  |  | 10 |  | 749.9993 |  | 0.31244
BLD2PST |  | NurseStn_Lobby_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.0801 | 0 | 13.0064 | 79.9999 | 15.6443 | 11.1945 |  |  | 10 |  | 2467.3419 |  | 0.095647
BLD2PST |  | Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2002 | 0 | 18.5806 | 49.9999 | 15.2932 | 80.7294 | 304.9413 | 567.81 | 15 |  | 2202.9829 | 2501.3191 | 0.26781
BLD2PST |  | Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.5601 | 17.98 | 13.2719 | 5.2517 | 25.7922 | 10.7639 |  |  | 10 |  | 52.5171 |  | 0.98173
BLD2PST |  | Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.44627
BLD2PST |  | Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.5501 | 17.98 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.98187
BLD2PST |  | Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1 | 25.7922 | 10.7639 |  |  | 10 |  | 10 |  | 0.89241
BLD2PST |  | Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.0601 | 0 | 92.9031 | 5.4 | 14.6034 | 0 |  |  |  | 0.25 | 125.42 |  | 0.14878
BLD2PST | Total | Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 1291.1824 | 21.9082 | 17.4152 | 12.6348 | 1037.1996 |  | 1.8146 | 1.8146 |  | 0.22109
BLD2NEW |  | Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 11.8403 | 8.0729 |  |  | 10 |  | 1006.2497 |  | 0
BLD2NEW |  | ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 29.0625 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.23806
BLD2NEW |  | ER_Trauma1_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 29.0625 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
BLD2NEW |  | ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 4.6452 | 5.9998 | 29.0625 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.1785
BLD2NEW |  | ER_Trauma2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 29.0625 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
BLD2NEW |  | ER_Triage_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 29.0625 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.23806
BLD2NEW |  | Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1.0503 | 11.8403 | 11.8403 |  |  | 10 |  | 10.5034 |  | 0.23798
BLD2NEW |  | Lobby_Records_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.7804 | 62.6301 | 13.0064 | 113.3908 | 15.8229 | 1.0764 |  |  | 10 |  | 1133.9077 |  | 0.070849
BLD2NEW |  | Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 10.7639 | 0 |  |  |  | 0.25 | 1349.325 |  | 0.040809
BLD2NEW |  | ER_NurseStn_Lobby_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.5801 | 30.42 | 14.8645 | 83.1249 | 12.0556 | 14.6389 |  |  |  |  | 2929.9675 |  | 0.02282
BLD2NEW |  | OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.0501 | 0 | 18.5806 | 2.9999 | 23.6806 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.29758
BLD2NEW |  | OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 23.6806 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.11903
BLD2NEW |  | OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 23.6806 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.17855
BLD2NEW |  | OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 23.6806 | 53.8195 |  | 7.5708 |  |  | 793.0838 |  | 0
BLD2NEW |  | IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 8.6111 | 32.2917 |  |  |  |  | 49.5596 |  | 0.23803
BLD2NEW |  | IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 8.6111 | 32.2917 |  |  |  |  | 66.0874 |  | 0.41656
BLD2NEW |  | IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 8.6111 | 32.2917 |  |  |  |  | 49.5596 |  | 0.23803
BLD2NEW |  | ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.6802 | 25.03 | 4.6452 | 133.0332 | 8.6111 | 32.2917 |  |  |  |  | 1465.3513 |  | 0.088583
BLD2NEW |  | ICU_NurseStn_Lobby_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 12.0556 | 21.5278 |  |  | 10 |  | 1585.8356 |  | 0
BLD2NEW |  | Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 10.7639 | 0 |  |  | 10 | 0.25 | 1349.325 |  | 0.040809
BLD2NEW |  | OR_NurseStn_Lobby_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.1402 | 35.76 | 13.0064 | 77.8568 | 12.7014 | 11.1945 |  |  | 10 |  | 2401.245 |  | 0.045864
BLD2NEW |  | PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
BLD2NEW |  | PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 0.38087
BLD2NEW |  | PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
BLD2NEW |  | PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 0.38087
BLD2NEW |  | PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
BLD2NEW |  | PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 9.6875 | 16.1458 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
BLD2NEW |  | PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
BLD2NEW |  | PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
BLD2NEW |  | PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
BLD2NEW |  | NurseStn_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 12.7014 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
BLD2NEW |  | Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 15.0695 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
BLD2NEW |  | Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.7639 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.020486
BLD2NEW |  | Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.7639 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.020486
BLD2NEW |  | PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
BLD2NEW |  | PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 0.38087
BLD2NEW |  | PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
BLD2NEW |  | PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 0.38087
BLD2NEW |  | PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.23803
BLD2NEW |  | Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 4.3056 | 107.639 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
BLD2NEW |  | PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
BLD2NEW |  | PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.23808
BLD2NEW |  | PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 7.5347 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.41656
BLD2NEW |  | NurseStn_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 12.7014 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
BLD2NEW |  | Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 15.0695 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
BLD2NEW |  | Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.7639 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.020486
BLD2NEW |  | Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 10.7639 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.020486
BLD2NEW |  | Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.6702 | 35.76 | 9.2903 | 74.9999 | 9.6875 | 10.7639 |  |  | 10 |  | 749.9993 |  | 0.083317
BLD2NEW |  | NurseStn_Lobby_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.0801 | 0 | 13.0064 | 79.9999 | 12.7014 | 11.1945 |  |  | 10 |  | 2467.3419 |  | 0.025506
BLD2NEW |  | Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2002 | 0 | 18.5806 | 49.9999 | 12.9167 | 80.7294 | 304.9413 | 567.81 | 15 |  | 2202.9829 | 2501.3191 | 0.071417
BLD2NEW |  | Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.5601 | 17.98 | 13.2719 | 5.2517 | 11.8403 | 10.7639 |  |  | 10 |  | 52.5171 |  | 0.26179
BLD2NEW |  | Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 13.2719 | 5.2502 | 11.8403 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.119
BLD2NEW |  | Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.5501 | 17.98 | 13.2719 | 5.2502 | 11.8403 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.26183
BLD2NEW |  | Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1 | 11.8403 | 10.7639 |  |  | 10 |  | 10 |  | 0.23798
BLD2NEW |  | Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.0601 | 0 | 92.9031 | 5.4 | 10.7639 | 0 |  |  |  | 0.25 | 125.42 |  | 0.039676
BLD2NEW | Total | Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 1291.1824 | 12.0581 | 17.4152 | 12.6348 | 1037.1996 |  |  |  |  | 0.058957

## LocationSummary
BLD | UWG | Location Summary
BLD | UWG |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD2PRE |  | Program
BLD2PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD2PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD2PRE
BLD2PRE |  | Fabric
BLD2PRE |  |  | Exterior walls
BLD2PRE | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD2PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD2PRE |  |  | Underground walls
BLD2PRE |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD2PRE |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675
BLD2PRE |  |  | Roof
BLD2PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD2PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD2PRE |  |  | Window
BLD2PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD2PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD2PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD2PRE |  |  | Skylights/TDD
BLD2PRE |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2PRE |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2PRE |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2PRE |  |  | Foundation
BLD2PRE |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD2PRE |  |  | Construction | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab
BLD2PRE |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD2PRE |  | HVAC
BLD2PRE |  |  | HVAC Sizing
BLD2PRE |  |  | Air Conditioning (kW)
BLD2PRE | HVAC |  | COOLSYS1 CHILLER | 3415.7574 | 3397.9324 | 3123.5546 | 3196.8153 | 2658.5769 | 2763.8652 | 2284.6301 | 3213.1319 | 2303.1765 | 2402.4192 | 3061.0916 | 2184.888 | 2948.6261 | 2079.523 | 2572.8197 | 2020.0632
BLD2PRE |  |  | Heating (kW)
BLD2PRE | HEAT |  | HEATSYS1 BOILER | 3494.7069 | 3682.0495 | 3665.5622 | 3703.9411 | 3375.9573 | 3602.6455 | 3348.3746 | 3807.0237 | 3350.7745 | 3580.51 | 3779.9148 | 3301.4912 | 3865.9818 | 3569.0303 | 3785.1825 | 4162.8318
BLD2PRE |  |  | HVAC Efficiency
BLD2PRE | COP |  | Air Conditioning (COP) | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54
BLD2PRE | EffHeat |  | Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
BLD2PRE |  |  | HVAC Control - Economizer
BLD2PRE |  |  | CAV_1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD2PRE |  |  | CAV_2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD2PRE |  |  | VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD2PRE |  |  | VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD2PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 114.14 | 115.49 | 120.79 | 117.24 | 109.28 | 120.97 | 105.33 | 113.02 | 121.84 | 109.38 | 107.36 | 113.96 | 106.18 | 109.45 | 103.22 | 98.59
BLD2PRE |  |  | CAV_1_FAN | 18.82 | 19.06 | 20.84 | 19.36 | 18.05 | 20.75 | 18.06 | 19.05 | 19.67 | 18.82 | 17.14 | 17.38 | 17.1 | 17.25 | 16.63 | 16.48
BLD2PRE |  |  | CAV_2_FAN | 16.15 | 16.15 | 17.19 | 16.66 | 15.53 | 17.49 | 15.3 | 16.07 | 18.45 | 15.83 | 15.92 | 17.94 | 15.99 | 17.15 | 15.88 | 15.31
BLD2PRE |  |  | VAV_1_FAN | 30.42 | 30.57 | 30.46 | 30.92 | 28.85 | 30.61 | 26.48 | 29.79 | 31.69 | 27.98 | 28.2 | 29.64 | 28.06 | 28.4 | 26.21 | 23.83
BLD2PRE |  |  | VAV_2_FAN | 48.75 | 49.71 | 52.3 | 50.3 | 46.85 | 52.12 | 45.49 | 48.11 | 52.03 | 46.75 | 46.1 | 49 | 45.03 | 46.65 | 44.5 | 42.97
BLD2PRE |  | Utility Costs
BLD2PRE |  |  | Electric Utility Rates
BLD2PRE |  |  | Average Annual Rate ($/kWh) | 0.072222 | 0.090732 | 0.062465 | 0.094254 | 0.038933 | 0.083272 | 0.12178 | 0.049704 | 0.036945 | 0.063319 | 0.10046 | 0.036946 | 0.048911 | 0.066916 | 0.049551 | 0.08677
BLD2PRE |  |  | Total Cost ($/m2) | 42.05 | 53.44 | 36.32 | 54.51 | 20.54 | 46.48 | 60.73 | 28.54 | 18.73 | 32.23 | 52.16 | 17.82 | 24.35 | 31.16 | 23.12 | 36.14
BLD2PRE |  |  | Gas Utility Rates
BLD2PRE |  |  | Average Annual Rate ($/MJ) | 0.011447 | 0.0081767 | 0.0085673 | 0.010691 | 0.0084115 | 0.0081012 | 0.0084127 | 0.010063 | 0.0071592 | 0.008296 | 0.0088778 | 0.0071634 | 0.0079671 | 0.0086657 | 0.0079638 | 0.0041713
BLD2PRE |  |  | Total Cost ($/m2) | 6.22 | 5.15 | 5.43 | 7.49 | 5.22 | 5.11 | 5.81 | 7.81 | 4.12 | 6.54 | 6.48 | 4.02 | 6.25 | 5.71 | 6.59 | 4.75
BLD2PRE |  |  | Total Utility Costs
BLD2PRE |  |  | Cost Intensity ($/m2) | 48.27 | 58.6 | 41.75 | 62 | 25.76 | 51.6 | 66.54 | 36.35 | 22.85 | 38.78 | 58.63 | 21.83 | 30.6 | 36.86 | 29.71 | 40.89
BLD2PRE |  | Energy - End Uses
BLD2PRE |  |  | Electricity (kWh)
BLD2PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Cooling | 6041913.8889 | 6144113.8889 | 5670177.7778 | 5807797.2222 | 5020475 | 4880800 | 4532091.6667 | 5637280.5556 | 3915866.6667 | 4570638.8889 | 4527244.4444 | 3545466.6667 | 4022738.8889 | 3253083.3333 | 3336769.4444 | 2199008.3333
BLD2PRE |  |  | Interior Lighting | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667
BLD2PRE |  |  | Exterior Lighting | 91075 | 90913.8889 | 90886.1111 | 91038.8889 | 91022.2222 | 90933.3333 | 90836.1111 | 90927.7778 | 90913.8889 | 90777.7778 | 90802.7778 | 90819.4444 | 90877.7778 | 90766.6667 | 90741.6667 | 90200
BLD2PRE |  |  | Interior Equipment | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444
BLD2PRE |  |  | Exterior Equipment | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667
BLD2PRE |  |  | Fans | 1111300 | 1104200 | 1204191.6667 | 1121686.1111 | 1043163.8889 | 1204102.7778 | 1025125 | 1083111.1111 | 1191336.1111 | 1060836.1111 | 1010316.6667 | 1086363.8889 | 1010566.6667 | 1050011.1111 | 985736.1111 | 968341.6667
BLD2PRE |  |  | Pumps | 536961.1111 | 515213.8889 | 460500 | 470233.3333 | 402850 | 406288.8889 | 331730.5556 | 457736.1111 | 336138.8889 | 340972.2222 | 414844.4444 | 307313.8889 | 384572.2222 | 281461.1111 | 319986.1111 | 213788.8889
BLD2PRE |  |  | Heat Rejection | 370891.6667 | 365561.1111 | 338133.3333 | 334836.1111 | 288675 | 295269.4444 | 248055.5556 | 318897.2222 | 231336.1111 | 258072.2222 | 264100 | 202208.3333 | 228302.7778 | 181538.8889 | 182536.1111 | 117161.1111
BLD2PRE |  |  | Humidification | 7797.2222 | 94700 | 380516.6667 | 250661.1111 | 93016.6667 | 748366.6667 | 64988.8889 | 398855.5556 | 712086.1111 | 205291.6667 | 445300 | 694236.1111 | 539569.4444 | 695722.2222 | 658444.4444 | 863800
BLD2PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Refrigeration | 56830.5556 | 54613.8889 | 54802.7778 | 52597.2222 | 53072.2222 | 53152.7778 | 51533.3333 | 51275 | 51116.6667 | 50333.3333 | 50436.1111 | 50083.3333 | 50016.6667 | 49319.4444 | 48650 | 47713.8889
BLD2PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total End Uses | 13054627.7778 | 13207175 | 13037061.1111 | 12966705.5556 | 11830130.5556 | 12516766.6667 | 11182213.8889 | 12875941.6667 | 11366650 | 11414775 | 11640902.7778 | 10814347.2222 | 11164497.2222 | 10439758.3333 | 10460716.6667 | 9337869.4444
BLD2PRE |  |  | Gas (MJ)
BLD2PRE |  |  | Heating | 10372910 | 12231090 | 12366960 | 13729090 | 11945840 | 12232100 | 13443620 | 15343140 | 10856460 | 15586420 | 14238060 | 10453230 | 15412790 | 12588580 | 16305680 | 23191490
BLD2PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Equipment | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420
BLD2PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Water Systems | 453040 | 543380 | 491450 | 630470 | 613600 | 554010 | 688100 | 698910 | 685920 | 734550 | 759010 | 755890 | 810920 | 820360 | 896590 | 1000220
BLD2PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total End Uses | 12184370 | 14132890 | 14216820 | 15717980 | 13917850 | 14144530 | 15490140 | 17400470 | 12900800 | 17679390 | 16355490 | 12567540 | 17582130 | 14767360 | 18560690 | 25550120
BLD2PRE |  |  | Purchased Cooling (MJ)
BLD2PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Purchased Heating (MJ)
BLD2PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total Building (MJ) | 59181030 | 61678710 | 61150250 | 62398120 | 56506330 | 59204890 | 55746100 | 63753860 | 53820740 | 58772580 | 58262730 | 51499190 | 57774320 | 52350490 | 56219270 | 59166450
BLD2PRE |  | Energy - End Use Intensities
BLD2PRE |  |  | Electricity (MJ/m2)
BLD2PRE |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Cooling (elec) | 970.0587 | 986.4675 | 910.3747 | 932.4702 | 806.0617 | 783.6362 | 727.6494 | 905.0929 | 628.7115 | 733.8384 | 726.8712 | 569.242 | 645.8704 | 522.2984 | 535.7346 | 353.0615
BLD2PRE |  |  | Interior Lighting (elec) | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135
BLD2PRE |  |  | Exterior Lighting (elec) | 14.6225 | 14.5967 | 14.5922 | 14.6167 | 14.6141 | 14.5998 | 14.5842 | 14.5989 | 14.5967 | 14.5748 | 14.5788 | 14.5815 | 14.5909 | 14.573 | 14.569 | 14.482
BLD2PRE |  |  | Interior Equipment (elec) | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554
BLD2PRE |  |  | Exterior Equipment (elec) | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719
BLD2PRE |  |  | Fans (elec) | 178.4246 | 177.2847 | 193.3388 | 180.0922 | 167.4851 | 193.3246 | 164.5888 | 173.8988 | 191.2748 | 170.3224 | 162.2113 | 174.421 | 162.2514 | 168.5844 | 158.2647 | 155.472
BLD2PRE |  |  | Pumps (elec) | 86.2117 | 82.7201 | 73.9355 | 75.4983 | 64.6795 | 65.2317 | 53.261 | 73.4918 | 53.9687 | 54.7448 | 66.6053 | 49.3407 | 61.7449 | 45.19 | 51.3753 | 34.3248
BLD2PRE |  |  | Heat Rejection (elec) | 59.5485 | 58.6926 | 54.289 | 53.7596 | 46.3482 | 47.4069 | 39.8265 | 51.2005 | 37.1421 | 41.4348 | 42.4025 | 32.4655 | 36.6551 | 29.147 | 29.3071 | 18.8108
BLD2PRE |  |  | Humidification (elec) | 1.2519 | 15.2045 | 61.0938 | 40.2449 | 14.9343 | 120.1539 | 10.4343 | 64.0382 | 114.3289 | 32.9606 | 71.4951 | 111.463 | 86.6305 | 111.7016 | 105.7165 | 138.6873
BLD2PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Refrigeration (elec) | 9.1244 | 8.7685 | 8.7989 | 8.4447 | 8.521 | 8.5339 | 8.2739 | 8.2325 | 8.207 | 8.0813 | 8.0978 | 8.0411 | 8.0304 | 7.9185 | 7.811 | 7.6607
BLD2PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total End Uses | 2095.9842 | 2120.4764 | 2093.1638 | 2081.8678 | 1899.3852 | 2009.6279 | 1795.359 | 2067.2952 | 1824.9711 | 1832.6978 | 1869.0037 | 1736.2962 | 1792.5145 | 1676.1541 | 1679.5191 | 1499.2405
BLD2PRE |  |  | Gas (MJ/m2)
BLD2PRE |  |  | Heating (gas) | 462.617 | 545.4892 | 551.5488 | 612.2979 | 532.7675 | 545.5343 | 599.5663 | 684.2822 | 484.1827 | 695.1322 | 634.9972 | 466.1992 | 687.3885 | 561.4328 | 727.2101 | 1034.3075
BLD2PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Equipment (gas) | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836
BLD2PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Water Systems (gas) | 20.2049 | 24.234 | 21.918 | 28.1181 | 27.3657 | 24.7081 | 30.6883 | 31.1704 | 30.5911 | 32.7599 | 33.8508 | 33.7116 | 36.1659 | 36.5869 | 39.9866 | 44.6084
BLD2PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total End Uses | 543.4056 | 630.3068 | 634.0499 | 700.9995 | 620.7163 | 630.8259 | 690.8382 | 776.0362 | 575.3573 | 788.4756 | 729.4316 | 560.4944 | 784.138 | 658.6032 | 827.7804 | 1139.499
BLD2PRE |  |  | Purchased Cooling (MJ/m2)
BLD2PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Purchased Heating (MJ/m2)
BLD2PRE |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Total Building (MJ/m2) | 2639.3897 | 2750.7827 | 2727.2141 | 2782.8674 | 2520.1019 | 2640.4539 | 2486.1967 | 2843.3314 | 2400.3284 | 2621.1734 | 2598.4349 | 2296.7906 | 2576.6525 | 2334.7574 | 2507.2994 | 2638.7395
BLD2PRE |  | Peak Energy Demand
BLD2PRE |  |  | Electricity Peak Demand (kW)
BLD2PRE |  |  | Jan | 1983.1578 | 2051.3623 | 2002.91 | 1976.5924 | 1842.2066 | 1957.7459 | 1729.748 | 1991.6309 | 1816.3479 | 1761.8674 | 1847.3809 | 1762.9494 | 1602.4747 | 1654.3415 | 1600.4967 | 1622.8198
BLD2PRE |  |  | Feb | 1948.9253 | 2003.9637 | 2024.6185 | 1950.8314 | 1819.4482 | 1947.6641 | 1704.4798 | 1971.4916 | 1832.6547 | 1770.8792 | 1863.2222 | 1757.7048 | 1653.4221 | 1728.8629 | 1773.7655 | 1629.1086
BLD2PRE |  |  | Mar | 1997.5882 | 1996.5885 | 1941.0508 | 1934.8873 | 1827.0031 | 1947.3021 | 1724.1062 | 1992.5513 | 1841.7148 | 1748.8095 | 1881.4442 | 1770.5101 | 1888.4111 | 1691.5669 | 1699.7939 | 1625.6453
BLD2PRE |  |  | Apr | 1960.8656 | 1969.6171 | 1968.0254 | 1902.8331 | 1790.9245 | 1878.2838 | 1686.1668 | 1947.5635 | 1775.2981 | 1739.7329 | 1946.7374 | 1734.1942 | 1897.3103 | 1700.1018 | 1795.2552 | 1654.966
BLD2PRE |  |  | May | 1898.9938 | 1908.7242 | 1896.0427 | 1892.944 | 1768.6805 | 1898.6553 | 1687.8255 | 1929.9964 | 1751.7442 | 1709.3569 | 1912.9533 | 1718.0999 | 1874.6358 | 1670.2901 | 1798.302 | 1657.0907
BLD2PRE |  |  | Jun | 1849.1324 | 1822.1396 | 1905.9088 | 1842.7897 | 1728.2255 | 1823.9924 | 1677.7461 | 1876.8531 | 1733.6786 | 1709.5174 | 1889.7433 | 1696.6398 | 1856.8924 | 1684.7406 | 1795.3184 | 1637.749
BLD2PRE |  |  | Jul | 1830.7721 | 1823.3724 | 1824.6196 | 1822.8532 | 1657.4823 | 1826.1935 | 1664.3657 | 1840.651 | 1702.8463 | 1687.2948 | 1798.6525 | 1625.0111 | 1809.6026 | 1598.4213 | 1749.4871 | 1586.879
BLD2PRE |  |  | Aug | 1827.4138 | 1872.7922 | 1796.8493 | 1813.9812 | 1665.5248 | 1794.2635 | 1657.0374 | 1851.5663 | 1635.3816 | 1670.6356 | 1852.7812 | 1619.8185 | 1790.8469 | 1638.072 | 1761.4043 | 1603.7343
BLD2PRE |  |  | Sep | 1868.3614 | 1879.3804 | 1825.7948 | 1825.6213 | 1699.5935 | 1806.6748 | 1641.4217 | 1881.692 | 1686.5528 | 1700.1206 | 1896.9059 | 1692.9381 | 1858.6034 | 1649.8165 | 1802.1283 | 1615.5515
BLD2PRE |  |  | Oct | 1880.2595 | 1926.5058 | 1936.5882 | 1916.846 | 1778.9999 | 1868.2675 | 1656.7392 | 1964.5549 | 1808.7007 | 1721.2189 | 1962.7661 | 1737.9545 | 1881.8153 | 1683.4128 | 1785.5032 | 1639.6347
BLD2PRE |  |  | Nov | 1911.8044 | 2010.0113 | 1937.0901 | 1972.8874 | 1827.2652 | 1939.791 | 1715.9848 | 1982.1982 | 1831.1092 | 1754.589 | 1881.1664 | 1774.1146 | 1906.4734 | 1704.9305 | 1824.3339 | 1525.5927
BLD2PRE |  |  | Dec | 1948.1441 | 2021.9615 | 2013.3395 | 1991.3405 | 1885.276 | 1950.1528 | 1755.057 | 1961.9759 | 1804.6991 | 1731.9046 | 1840.8699 | 1753.256 | 1667.5261 | 1687.2469 | 1564.2664 | 1607.7277
BLD2PRE |  |  | Time of Peak Electrical Demand
BLD2PRE |  |  | Jan | 12-JAN-09:15 | 09-JAN-17:00 | 23-JAN-17:00 | 20-JAN-17:00 | 18-JAN-14:00 | 30-JAN-17:30 | 20-JAN-13:15 | 05-JAN-16:00 | 20-JAN-17:30 | 03-JAN-17:00 | 17-JAN-14:45 | 24-JAN-17:00 | 30-JAN-17:00 | 25-JAN-17:15 | 13-JAN-16:45 | 19-JAN-10:30
BLD2PRE |  |  | Feb | 10-FEB-17:00 | 08-FEB-15:30 | 21-FEB-13:30 | 23-FEB-17:00 | 27-FEB-10:30 | 01-FEB-17:15 | 23-FEB-17:00 | 28-FEB-17:00 | 15-FEB-17:00 | 21-FEB-17:00 | 28-FEB-11:45 | 07-FEB-17:00 | 17-FEB-16:15 | 03-FEB-17:00 | 28-FEB-17:00 | 28-FEB-16:45
BLD2PRE |  |  | Mar | 15-MAR-08:15 | 14-MAR-16:00 | 03-MAR-10:15 | 14-MAR-09:00 | 22-MAR-16:00 | 06-MAR-17:00 | 03-MAR-17:00 | 10-MAR-17:00 | 03-MAR-17:00 | 03-MAR-17:00 | 30-MAR-15:45 | 31-MAR-15:45 | 31-MAR-16:45 | 31-MAR-16:00 | 21-MAR-15:45 | 30-MAR-16:00
BLD2PRE |  |  | Apr | 06-APR-08:15 | 07-APR-09:00 | 20-APR-08:15 | 26-APR-09:00 | 11-APR-15:00 | 13-APR-08:15 | 21-APR-16:30 | 21-APR-16:00 | 11-APR-16:15 | 25-APR-15:15 | 27-APR-16:00 | 07-APR-16:00 | 13-APR-16:00 | 04-APR-16:00 | 27-APR-15:45 | 25-APR-16:00
BLD2PRE |  |  | May | 02-MAY-08:15 | 10-MAY-08:15 | 16-MAY-16:45 | 09-MAY-09:15 | 19-MAY-09:00 | 05-MAY-09:15 | 19-MAY-16:00 | 18-MAY-15:00 | 05-MAY-16:00 | 11-MAY-15:15 | 12-MAY-15:00 | 09-MAY-15:00 | 17-MAY-16:00 | 18-MAY-10:15 | 12-MAY-16:00 | 09-MAY-15:15
BLD2PRE |  |  | Jun | 02-JUN-16:00 | 30-JUN-16:00 | 19-JUN-10:45 | 12-JUN-09:15 | 01-JUN-08:45 | 20-JUN-15:00 | 02-JUN-16:00 | 20-JUN-10:00 | 27-JUN-16:00 | 01-JUN-16:00 | 23-JUN-15:00 | 15-JUN-16:00 | 14-JUN-10:45 | 01-JUN-16:00 | 23-JUN-16:00 | 02-JUN-10:45
BLD2PRE |  |  | Jul | 25-JUL-15:00 | 28-JUL-16:00 | 06-JUL-10:00 | 05-JUL-10:45 | 12-JUL-15:00 | 31-JUL-16:00 | 06-JUL-10:45 | 20-JUL-09:15 | 31-JUL-16:00 | 03-JUL-15:00 | 05-JUL-10:45 | 12-JUL-15:00 | 31-JUL-10:45 | 13-JUL-08:15 | 21-JUL-09:30 | 27-JUL-08:15
BLD2PRE |  |  | Aug | 11-AUG-15:00 | 09-AUG-10:45 | 16-AUG-10:00 | 30-AUG-08:15 | 09-AUG-16:00 | 15-AUG-10:00 | 03-AUG-08:15 | 23-AUG-09:15 | 29-AUG-16:00 | 10-AUG-09:15 | 07-AUG-08:15 | 25-AUG-16:00 | 11-AUG-08:00 | 31-AUG-09:15 | 31-AUG-16:00 | 28-AUG-16:00
BLD2PRE |  |  | Sep | 21-SEP-09:00 | 26-SEP-10:45 | 22-SEP-06:15 | 26-SEP-08:15 | 21-SEP-07:15 | 29-SEP-16:00 | 12-SEP-08:15 | 22-SEP-14:00 | 20-SEP-16:00 | 19-SEP-16:00 | 20-SEP-15:00 | 26-SEP-10:45 | 28-SEP-16:00 | 14-SEP-10:15 | 27-SEP-15:15 | 28-SEP-16:00
BLD2PRE |  |  | Oct | 24-OCT-08:15 | 16-OCT-08:15 | 16-OCT-08:15 | 23-OCT-10:15 | 30-OCT-07:15 | 30-OCT-16:00 | 24-OCT-09:15 | 24-OCT-16:00 | 31-OCT-16:00 | 16-OCT-16:00 | 26-OCT-16:00 | 17-OCT-15:15 | 19-OCT-15:15 | 17-OCT-15:15 | 19-OCT-15:15 | 03-OCT-16:00
BLD2PRE |  |  | Nov | 22-NOV-09:15 | 29-NOV-17:00 | 16-NOV-09:15 | 15-NOV-17:00 | 24-NOV-17:00 | 24-NOV-17:45 | 20-NOV-16:00 | 07-NOV-17:45 | 13-NOV-17:00 | 21-NOV-16:00 | 01-NOV-16:00 | 10-NOV-17:45 | 01-NOV-16:00 | 21-NOV-16:45 | 03-NOV-16:00 | 14-NOV-09:15
BLD2PRE |  |  | Dec | 01-DEC-17:00 | 12-DEC-17:30 | 27-DEC-17:00 | 06-DEC-17:00 | 08-DEC-16:00 | 04-DEC-17:30 | 29-DEC-16:00 | 08-DEC-16:00 | 05-DEC-16:00 | 07-DEC-17:00 | 12-DEC-11:45 | 29-DEC-16:00 | 01-DEC-13:00 | 01-DEC-16:45 | 01-DEC-16:30 | 18-DEC-10:00
BLD2PRE |  | Source Energy
BLD2PRE |  |  | Total Source Energy (GJ) | 169193.24 | 188119.55 | 163975.19 | 174196.03 | 147009.62 | 176626.74 | 141507.45 | 184761.03 | 149860.03 | 90890.23 | 166463.29 | 142898.96 | 157340.25 | 146764.93 | 149700.82 | 147978.26
BLD2PRE |  |  | Total Source Energy (MJ/m2) | 7545.78 | 8389.86 | 7313.06 | 7768.9 | 6556.42 | 7877.3 | 6311.03 | 8240.08 | 6683.54 | 4053.58 | 7424.03 | 6373.09 | 7017.15 | 6545.51 | 6676.44 | 6599.62
BLD2PRE |  | Water Consumption (m3)
BLD2PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Heat Rejection | 40986.87 | 35138.46 | 44241.81 | 29945.33 | 25034.72 | 38445.61 | 17666.9 | 26471.51 | 24936.34 | 17372.63 | 21036.73 | 19820.13 | 18668.46 | 15806.26 | 13164.77 | 8829.24
BLD2PRE |  |  | Humidification | 10.44 | 126.82 | 509.59 | 335.69 | 124.57 | 1002.21 | 87.03 | 534.15 | 953.63 | 274.92 | 596.35 | 929.72 | 722.59 | 931.71 | 881.79 | 1156.8
BLD2PRE |  |  | Water Systems | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67
BLD2PRE |  |  | Total Building | 45002.98 | 39270.95 | 48757.07 | 34286.69 | 29164.96 | 43453.49 | 21759.6 | 31011.33 | 29895.64 | 21653.23 | 25638.75 | 24755.52 | 23396.72 | 20743.65 | 18052.23 | 13991.71
BLD2PRE |  | Emissions
BLD2PRE |  |  | Carbon Equivalent (kg) | 3799950 | 4660250 | 4191940 | 4277660 | 1633510 | 4476660 | 1586150 | 3788420 | 4875890 | 1150190 | 6501270 | 4644270 | 4138580 | 4081370 | 3915330 | 3088300
BLD2PRE |  |  | CO2 (kg) | 8925020 | 11790700 | 9995970 | 9884190 | 4416260 | 10735800 | 4296020 | 8698570 | 11491400 | 2896040 | 15171800 | 10948300 | 9726160 | 9642760 | 9221770 | 7913240
BLD2PRE |  |  | NOX (kg) | 15196.9802 | 15198.4899 | 16315.3656 | 18248.514 | 3817.1015 | 17066.502 | 3718.4685 | 16402.4159 | 19592.9676 | 4009.4514 | 26848.3034 | 18654.8365 | 16908.5118 | 16449.5872 | 15941.3542 | 9454.6063
BLD2PRE |  |  | SO2 (kg) | 55882.2883 | 63002.0066 | 52428.4434 | 45517.352 | 34427.9932 | 68856.0245 | 32543.0486 | 47006.9981 | 49639.3441 | 8827.4465 | 78454.7488 | 47227.4586 | 26354.7138 | 27879.3675 | 24693.942 | 47540.3378
BLD2PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PRE |  |  | Hg (kg) | 0.2559 | 0.1785 | 0.1437 | 0.1677 | 0.0169 | 0.1305 | 0.0163 | 0.1912 | 0.1947 | 0.0362 | 0.2381 | 0.1852 | 0.194 | 0.1948 | 0.182 | 0.1635
BLD2PRE |  |  | Water for Electricity (m3) | 6915.79 | 21489.6 | 387258 | 80958.9 | 207711 | 343385 | 196335 | 2923.32 | 51613.7 | 116622 | 18060.2 | 49105.8 | 17321.1 | 661298 | 16229.2 | 9540.31
BLD2PST |  | Fabric
BLD2PST |  |  | Exterior walls
BLD2PST | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD2PST | RvalWall |  | R-value (m2·K / W) | 2.377 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
BLD2PST |  |  | Underground walls
BLD2PST |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD2PST |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 1.5385 | 0.30675 | 0.30675 | 1.5385 | 1.8904 | 1.7123 | 1.8904 | 2.0661 | 2.0661 | 2.4155 | 2.2422 | 2.5974 | 3.125
BLD2PST |  |  | Roof
BLD2PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD2PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD2PST |  |  | Window
BLD2PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD2PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD2PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD2PST |  |  | Skylights/TDD
BLD2PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2PST |  |  | Foundation
BLD2PST |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD2PST |  |  | Construction | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab
BLD2PST |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD2PST |  | HVAC
BLD2PST |  |  | HVAC Sizing
BLD2PST |  |  | Air Conditioning (kW)
BLD2PST | HVAC |  | COOLSYS1 CHILLER | 3317.7354 | 3272.1969 | 2992.1053 | 3052.2014 | 2637.6716 | 2600.8729 | 2214.0284 | 3052.2193 | 2185.9303 | 2281.7485 | 3019.3167 | 2147.4495 | 2905.9548 | 2050.9651 | 2569.7719 | 2078.5723
BLD2PST |  |  | Heating (kW)
BLD2PST | HEAT |  | HEATSYS1 BOILER | 3292.1556 | 3444.169 | 3450.4642 | 3463.4962 | 3283.1835 | 3332.8226 | 3191.185 | 3572.7157 | 3158.2495 | 3404.7626 | 3749.1716 | 3265.9071 | 3832.2463 | 3556.5715 | 3840.169 | 4321.1484
BLD2PST |  |  | HVAC Efficiency
BLD2PST | COP |  | Air Conditioning (COP) | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
BLD2PST | EffHeat |  | Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
BLD2PST |  |  | HVAC Control - Economizer
BLD2PST |  |  | CAV_1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD2PST |  |  | CAV_2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD2PST |  |  | VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD2PST |  |  | VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD2PST | Fan |  | Fan Max Flow Rate (m3/s ) | 109.36 | 108.93 | 113.52 | 109.53 | 108.33 | 111.41 | 101.71 | 104.6 | 114.4 | 102.77 | 105.04 | 111.7 | 103.83 | 107.71 | 102.97 | 101.52
BLD2PST |  |  | CAV_1_FAN | 17.09 | 17.09 | 18.94 | 16.8 | 17.38 | 18.06 | 16.6 | 16.58 | 17.51 | 16.83 | 16.81 | 17.14 | 16.71 | 16.88 | 17.11 | 18.22
BLD2PST |  |  | CAV_2_FAN | 15.97 | 15.91 | 17.17 | 16.28 | 15.37 | 17.22 | 14.96 | 15.57 | 18.09 | 15.5 | 15.8 | 17.9 | 15.84 | 17.1 | 15.94 | 15.56
BLD2PST |  |  | VAV_1_FAN | 29.68 | 29.45 | 29.83 | 29.36 | 28.83 | 29.01 | 25.74 | 27.92 | 30.35 | 26.27 | 28.05 | 29.75 | 27.81 | 28.34 | 26.69 | 25.39
BLD2PST |  |  | VAV_2_FAN | 46.62 | 46.48 | 47.58 | 47.09 | 46.75 | 47.12 | 44.41 | 44.53 | 48.45 | 44.17 | 44.38 | 46.91 | 43.47 | 45.39 | 43.23 | 42.35
BLD2PST |  | Utility Costs
BLD2PST |  |  | Electric Utility Rates
BLD2PST |  |  | Average Annual Rate ($/kWh) | 0.072201 | 0.090768 | 0.06245 | 0.09426 | 0.038797 | 0.083277 | 0.12172 | 0.049975 | 0.036945 | 0.063341 | 0.10044 | 0.036945 | 0.048928 | 0.0669 | 0.049505 | 0.086788
BLD2PST |  |  | Total Cost ($/m2) | 42.57 | 53.76 | 36.35 | 54.31 | 20.96 | 45.86 | 61.23 | 28.33 | 18.54 | 32.08 | 53.09 | 18.08 | 24.75 | 31.6 | 23.72 | 37.51
BLD2PST |  |  | Gas Utility Rates
BLD2PST |  |  | Average Annual Rate ($/MJ) | 0.011443 | 0.0081705 | 0.0085474 | 0.010664 | 0.0084165 | 0.0080861 | 0.0084171 | 0.010079 | 0.0071605 | 0.0082897 | 0.0088991 | 0.0071692 | 0.007977 | 0.0086961 | 0.0079732 | 0.0041782
BLD2PST |  |  | Total Cost ($/m2) | 5.43 | 4.6 | 4.81 | 6.5 | 5.08 | 4.45 | 5.48 | 6.54 | 3.6 | 5.53 | 6.16 | 3.86 | 5.82 | 5.34 | 6.22 | 4.57
BLD2PST |  |  | Total Utility Costs
BLD2PST |  |  | Cost Intensity ($/m2) | 48 | 58.36 | 41.16 | 60.82 | 26.04 | 50.32 | 66.7 | 34.87 | 22.14 | 37.61 | 59.25 | 21.95 | 30.57 | 36.94 | 29.95 | 42.08
BLD2PST |  | Energy - End Uses
BLD2PST |  |  | Electricity (kWh)
BLD2PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Cooling | 6291316.6667 | 6327405.5556 | 5806275 | 5917802.7778 | 5333411.1111 | 4916425 | 4704761.1111 | 5643586.1111 | 3966250 | 4629002.7778 | 4759355.5556 | 3723822.2222 | 4221366.6667 | 3422533.3333 | 3579569.4444 | 2426752.7778
BLD2PST |  |  | Interior Lighting | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667
BLD2PST |  |  | Exterior Lighting | 91075 | 90913.8889 | 90886.1111 | 91038.8889 | 91022.2222 | 90933.3333 | 90836.1111 | 90927.7778 | 90913.8889 | 90777.7778 | 90802.7778 | 90819.4444 | 90877.7778 | 90766.6667 | 90741.6667 | 90200
BLD2PST |  |  | Interior Equipment | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444
BLD2PST |  |  | Exterior Equipment | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667
BLD2PST |  |  | Fans | 1050097.2222 | 1028925 | 1133869.4444 | 1023011.1111 | 1017877.7778 | 1100808.3333 | 967747.2222 | 986611.1111 | 1102127.7778 | 987019.4444 | 998491.6667 | 1076816.6667 | 998786.1111 | 1041483.3333 | 1011933.3333 | 1041294.4444
BLD2PST |  |  | Pumps | 522341.6667 | 496483.3333 | 442780.5556 | 448083.3333 | 401408.3333 | 382502.7778 | 322527.7778 | 434172.2222 | 319716.6667 | 324766.6667 | 412483.3333 | 304838.8889 | 382250 | 279822.2222 | 323005.5556 | 222172.2222
BLD2PST |  |  | Heat Rejection | 363850 | 355044.4444 | 327152.7778 | 321372.2222 | 289269.4444 | 280572.2222 | 242791.6667 | 302705.5556 | 221719.4444 | 247530.5556 | 263952.7778 | 201636.1111 | 227830.5556 | 181480.5556 | 185627.7778 | 122941.6667
BLD2PST |  |  | Humidification | 7213.8889 | 87619.4444 | 357386.1111 | 227838.8889 | 90444.4444 | 686469.4444 | 60405.5556 | 362627.7778 | 660875 | 188041.6667 | 439116.6667 | 688458.3333 | 531252.7778 | 687075 | 668430.5556 | 902380.5556
BLD2PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Refrigeration | 57044.4444 | 54875 | 55077.7778 | 52772.2222 | 53069.4444 | 53394.4444 | 51586.1111 | 51430.5556 | 51455.5556 | 50519.4444 | 50444.4444 | 50205.5556 | 49969.4444 | 49244.4444 | 48597.2222 | 47677.7778
BLD2PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total End Uses | 13220791.6667 | 13279116.6667 | 13051286.1111 | 12919775 | 12114355.5556 | 12348961.1111 | 11278505.5556 | 12709916.6667 | 11250911.1111 | 11355511.1111 | 11852505.5556 | 10974452.7778 | 11340188.8889 | 10590258.3333 | 10745761.1111 | 9691275
BLD2PST |  |  | Gas (MJ)
BLD2PST |  |  | Heating | 8811250 | 10710350 | 10744110 | 11670030 | 11548980 | 10424190 | 12522680 | 12467270 | 9216260 | 12851960 | 13371500 | 9947810 | 14179610 | 11578470 | 15224430 | 22116480
BLD2PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Equipment | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420
BLD2PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Water Systems | 464640 | 557300 | 504030 | 646620 | 629310 | 568200 | 705730 | 716820 | 703520 | 753400 | 778460 | 775260 | 831690 | 841380 | 919530 | 1025850
BLD2PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total End Uses | 10634310 | 12626070 | 12606550 | 13675070 | 13536710 | 12350810 | 14586820 | 14542510 | 11278200 | 14963770 | 15508380 | 12081480 | 16369720 | 13778270 | 17502370 | 24500740
BLD2PST |  |  | Purchased Cooling (MJ)
BLD2PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Purchased Heating (MJ)
BLD2PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total Building (MJ) | 58229160 | 60430890 | 59591170 | 60186260 | 57148390 | 56807070 | 55189440 | 60298210 | 51781480 | 55843620 | 58177390 | 51589510 | 57194400 | 51903190 | 56187110 | 59389330
BLD2PST |  | Energy - End Use Intensities
BLD2PST |  |  | Electricity (MJ/m2)
BLD2PST |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Cooling (elec) | 1010.1016 | 1015.8958 | 932.2258 | 950.1321 | 856.3052 | 789.356 | 755.3723 | 906.1053 | 636.8008 | 743.209 | 764.1377 | 597.8778 | 677.761 | 549.5044 | 574.7173 | 389.627
BLD2PST |  |  | Interior Lighting (elec) | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135
BLD2PST |  |  | Exterior Lighting (elec) | 14.6225 | 14.5967 | 14.5922 | 14.6167 | 14.6141 | 14.5998 | 14.5842 | 14.5989 | 14.5967 | 14.5748 | 14.5788 | 14.5815 | 14.5909 | 14.573 | 14.569 | 14.482
BLD2PST |  |  | Interior Equipment (elec) | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554
BLD2PST |  |  | Exterior Equipment (elec) | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719
BLD2PST |  |  | Fans (elec) | 168.5982 | 165.1989 | 182.0483 | 164.2494 | 163.4252 | 176.7401 | 155.3765 | 158.4052 | 176.952 | 158.4708 | 160.3127 | 172.8882 | 160.36 | 167.2152 | 162.4708 | 167.1849
BLD2PST |  |  | Pumps (elec) | 83.8645 | 79.7128 | 71.0906 | 71.942 | 64.4481 | 61.4127 | 51.7834 | 69.7085 | 51.3321 | 52.1429 | 66.2262 | 48.9434 | 61.3721 | 44.9268 | 51.8601 | 35.6708
BLD2PST |  |  | Heat Rejection (elec) | 58.4179 | 57.0041 | 52.526 | 51.5979 | 46.4436 | 45.0472 | 38.9814 | 48.6009 | 35.5981 | 39.7422 | 42.3789 | 32.3737 | 36.5793 | 29.1376 | 29.8034 | 19.7389
BLD2PST |  |  | Humidification (elec) | 1.1582 | 14.0677 | 57.3801 | 36.5806 | 14.5213 | 110.216 | 9.6984 | 58.2217 | 106.1067 | 30.191 | 70.5023 | 110.5353 | 85.2952 | 110.3132 | 107.3198 | 144.8816
BLD2PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Refrigeration (elec) | 9.1588 | 8.8104 | 8.843 | 8.4728 | 8.5206 | 8.5727 | 8.2824 | 8.2574 | 8.2614 | 8.1111 | 8.0991 | 8.0607 | 8.0228 | 7.9064 | 7.8025 | 7.6549
BLD2PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total End Uses | 2122.6626 | 2132.027 | 2095.4476 | 2074.3329 | 1945.0189 | 1982.6859 | 1810.8191 | 2040.6391 | 1806.3887 | 1823.1827 | 1902.9776 | 1762.0019 | 1820.7226 | 1700.3176 | 1725.2844 | 1555.9815
BLD2PST |  |  | Gas (MJ/m2)
BLD2PST |  |  | Heating (gas) | 392.9692 | 477.6664 | 479.172 | 520.4667 | 515.0681 | 464.904 | 558.4937 | 556.0225 | 411.0321 | 573.1791 | 596.3499 | 443.6582 | 632.3904 | 516.3833 | 678.9879 | 986.3635
BLD2PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Equipment (gas) | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836
BLD2PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Water Systems (gas) | 20.7223 | 24.8548 | 22.479 | 28.8383 | 28.0663 | 25.3409 | 31.4746 | 31.9692 | 31.376 | 33.6006 | 34.7182 | 34.5755 | 37.0922 | 37.5244 | 41.0097 | 45.7515
BLD2PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total End Uses | 474.2751 | 563.1048 | 562.2342 | 609.8887 | 603.718 | 550.8286 | 650.5514 | 648.5753 | 502.9917 | 667.3629 | 691.6517 | 538.8168 | 730.0662 | 614.4912 | 780.5808 | 1092.6981
BLD2PST |  |  | Purchased Cooling (MJ/m2)
BLD2PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Purchased Heating (MJ/m2)
BLD2PST |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Total Building (MJ/m2) | 2596.9377 | 2695.1317 | 2657.6814 | 2684.2216 | 2548.7369 | 2533.5145 | 2461.3705 | 2689.2144 | 2309.3803 | 2490.546 | 2594.6288 | 2300.8187 | 2550.7889 | 2314.8084 | 2505.8652 | 2648.6796
BLD2PST |  | Peak Energy Demand
BLD2PST |  |  | Electricity Peak Demand (kW)
BLD2PST |  |  | Jan | 2010.1245 | 2058.4051 | 1999.8704 | 1967.0553 | 1875.5368 | 1935.3438 | 1732.8398 | 1977.512 | 1800.4223 | 1746.7142 | 1882.1986 | 1784.9747 | 1618.401 | 1676.3881 | 1641.8027 | 1685.9593
BLD2PST |  |  | Feb | 1971.7821 | 2018.7011 | 2027.3283 | 1948.748 | 1847.569 | 1923.7388 | 1712.4349 | 1960.9116 | 1816.7859 | 1765.056 | 1898.2977 | 1780.13 | 1671.7623 | 1752.6229 | 1818.4025 | 1693.7376
BLD2PST |  |  | Mar | 2022.3181 | 2012.7668 | 1945.2487 | 1933.6721 | 1857.2372 | 1924.3491 | 1734.3917 | 1982.8572 | 1825.6945 | 1740.2699 | 1914.4109 | 1793.7366 | 1920.7909 | 1711.3285 | 1748.8258 | 1689.4795
BLD2PST |  |  | Apr | 1983.6301 | 1986.0323 | 1970.9911 | 1910.0022 | 1816.2613 | 1858.5959 | 1695.842 | 1941.4039 | 1762.3918 | 1732.1818 | 1980.876 | 1757.2545 | 1931.6464 | 1722.0587 | 1840.6778 | 1719.9464
BLD2PST |  |  | May | 1921.8372 | 1927.7697 | 1889.0521 | 1905.9877 | 1802.8828 | 1875.6705 | 1700.1365 | 1934.7613 | 1742.6596 | 1705.9926 | 1949.9977 | 1740.0894 | 1908.7265 | 1693.6431 | 1839.2453 | 1722.6534
BLD2PST |  |  | Jun | 1866.0624 | 1829.2616 | 1899.83 | 1851.6549 | 1764.2952 | 1795.7252 | 1687.2601 | 1877.672 | 1718.4418 | 1707.171 | 1927.9152 | 1709.8163 | 1892.2963 | 1708.5132 | 1836.6112 | 1701.6076
BLD2PST |  |  | Jul | 1847.1424 | 1827.3973 | 1823.7084 | 1827.7983 | 1684.2121 | 1798.921 | 1675.3495 | 1841.1249 | 1679.0091 | 1687.306 | 1830.9659 | 1637.3176 | 1841.7542 | 1618.492 | 1796.7792 | 1642.2151
BLD2PST |  |  | Aug | 1844.0847 | 1885.944 | 1797.2077 | 1816.8622 | 1692.6857 | 1770.9698 | 1672.2089 | 1853.2951 | 1618.6902 | 1670.1521 | 1890.0591 | 1631.9552 | 1821.5699 | 1661.4511 | 1803.978 | 1657.9198
BLD2PST |  |  | Sep | 1887.2244 | 1893.6647 | 1833.1728 | 1831.6476 | 1735.5403 | 1779.4834 | 1656.1923 | 1880.5467 | 1665.9925 | 1700.2211 | 1936.6042 | 1716.4652 | 1894.2007 | 1673.0102 | 1848.2867 | 1679.5272
BLD2PST |  |  | Oct | 1903.1175 | 1943.5753 | 1940.9799 | 1930.8021 | 1811.7668 | 1845.4433 | 1669.0434 | 1952.9994 | 1790.7144 | 1717.3888 | 1999.5378 | 1759.7609 | 1914.6512 | 1706.4017 | 1831.4882 | 1704.5741
BLD2PST |  |  | Nov | 1937.6124 | 2024.3711 | 1937.9352 | 1972.5901 | 1860.3763 | 1914.6884 | 1723.3562 | 1977.4263 | 1818.8732 | 1745.9969 | 1919.6786 | 1797.6514 | 1940.5754 | 1728.4119 | 1871.8899 | 1591.7935
BLD2PST |  |  | Dec | 1970.8419 | 2025.9564 | 2010.2425 | 1983.7951 | 1917.7096 | 1929.448 | 1756.7926 | 1948.9741 | 1789.5315 | 1723.7183 | 1878.9867 | 1775.2489 | 1687.6905 | 1709.363 | 1601.8421 | 1664.0365
BLD2PST |  |  | Time of Peak Electrical Demand
BLD2PST |  |  | Jan | 12-JAN-17:00 | 09-JAN-17:45 | 23-JAN-17:00 | 20-JAN-17:00 | 18-JAN-14:00 | 30-JAN-17:30 | 17-JAN-17:00 | 05-JAN-16:00 | 20-JAN-17:30 | 03-JAN-17:00 | 17-JAN-14:45 | 25-JAN-17:45 | 30-JAN-17:00 | 25-JAN-17:15 | 13-JAN-16:45 | 19-JAN-16:30
BLD2PST |  |  | Feb | 10-FEB-17:00 | 08-FEB-15:30 | 21-FEB-13:30 | 22-FEB-17:00 | 14-FEB-17:00 | 06-FEB-17:00 | 23-FEB-17:00 | 28-FEB-17:00 | 15-FEB-17:00 | 21-FEB-17:00 | 28-FEB-11:45 | 07-FEB-17:00 | 17-FEB-16:15 | 03-FEB-17:45 | 28-FEB-17:00 | 28-FEB-17:00
BLD2PST |  |  | Mar | 15-MAR-08:15 | 29-MAR-15:00 | 03-MAR-10:15 | 14-MAR-10:45 | 22-MAR-16:00 | 06-MAR-17:00 | 03-MAR-17:00 | 10-MAR-17:45 | 03-MAR-17:00 | 23-MAR-15:00 | 30-MAR-15:45 | 31-MAR-15:45 | 31-MAR-16:45 | 31-MAR-16:00 | 21-MAR-15:00 | 30-MAR-16:00
BLD2PST |  |  | Apr | 06-APR-08:15 | 07-APR-09:00 | 20-APR-08:15 | 26-APR-09:00 | 04-APR-16:00 | 13-APR-08:15 | 21-APR-16:15 | 21-APR-16:00 | 11-APR-16:45 | 13-APR-15:00 | 27-APR-16:00 | 07-APR-16:00 | 13-APR-16:00 | 04-APR-16:00 | 27-APR-16:00 | 25-APR-16:00
BLD2PST |  |  | May | 02-MAY-08:15 | 10-MAY-08:15 | 16-MAY-15:45 | 09-MAY-09:15 | 19-MAY-09:00 | 05-MAY-09:30 | 19-MAY-16:00 | 18-MAY-15:00 | 05-MAY-16:00 | 11-MAY-15:15 | 12-MAY-15:00 | 09-MAY-15:00 | 17-MAY-16:00 | 18-MAY-10:15 | 03-MAY-16:00 | 09-MAY-15:15
BLD2PST |  |  | Jun | 02-JUN-16:00 | 05-JUN-10:45 | 19-JUN-10:45 | 12-JUN-09:15 | 01-JUN-08:45 | 19-JUN-09:00 | 02-JUN-16:45 | 20-JUN-10:00 | 26-JUN-16:00 | 08-JUN-10:45 | 23-JUN-15:00 | 15-JUN-16:00 | 14-JUN-10:45 | 01-JUN-16:00 | 23-JUN-16:00 | 02-JUN-10:45
BLD2PST |  |  | Jul | 25-JUL-15:00 | 28-JUL-16:00 | 06-JUL-10:00 | 05-JUL-10:45 | 12-JUL-15:00 | 31-JUL-16:00 | 06-JUL-10:45 | 20-JUL-09:15 | 31-JUL-16:00 | 03-JUL-15:00 | 05-JUL-10:45 | 12-JUL-15:00 | 31-JUL-10:45 | 13-JUL-08:15 | 21-JUL-09:30 | 27-JUL-08:15
BLD2PST |  |  | Aug | 01-AUG-12:15 | 09-AUG-10:45 | 16-AUG-10:00 | 30-AUG-08:15 | 09-AUG-16:00 | 15-AUG-10:00 | 03-AUG-08:15 | 23-AUG-09:15 | 29-AUG-16:00 | 10-AUG-09:15 | 07-AUG-08:15 | 25-AUG-16:00 | 11-AUG-08:00 | 31-AUG-09:15 | 31-AUG-16:00 | 28-AUG-16:00
BLD2PST |  |  | Sep | 21-SEP-09:00 | 18-SEP-10:45 | 22-SEP-06:15 | 26-SEP-08:15 | 21-SEP-07:15 | 29-SEP-16:00 | 12-SEP-08:15 | 22-SEP-14:00 | 20-SEP-16:00 | 19-SEP-16:00 | 20-SEP-15:00 | 26-SEP-10:45 | 28-SEP-16:00 | 14-SEP-10:15 | 27-SEP-15:45 | 28-SEP-16:00
BLD2PST |  |  | Oct | 24-OCT-08:15 | 16-OCT-09:15 | 16-OCT-08:15 | 23-OCT-09:45 | 30-OCT-07:15 | 30-OCT-16:00 | 02-OCT-09:15 | 24-OCT-16:45 | 31-OCT-16:00 | 16-OCT-16:00 | 26-OCT-16:00 | 17-OCT-15:15 | 19-OCT-15:15 | 17-OCT-15:15 | 19-OCT-15:15 | 03-OCT-16:00
BLD2PST |  |  | Nov | 22-NOV-09:15 | 29-NOV-17:00 | 16-NOV-09:15 | 16-NOV-17:00 | 24-NOV-17:00 | 24-NOV-17:45 | 20-NOV-16:00 | 07-NOV-16:00 | 13-NOV-17:00 | 21-NOV-16:00 | 01-NOV-16:00 | 10-NOV-17:45 | 01-NOV-16:00 | 21-NOV-16:45 | 03-NOV-16:00 | 14-NOV-09:15
BLD2PST |  |  | Dec | 26-DEC-17:00 | 12-DEC-17:30 | 27-DEC-17:45 | 27-DEC-17:45 | 08-DEC-16:00 | 14-DEC-16:00 | 29-DEC-16:00 | 08-DEC-16:00 | 05-DEC-16:00 | 07-DEC-17:00 | 12-DEC-17:00 | 29-DEC-16:00 | 01-DEC-13:00 | 01-DEC-16:45 | 01-DEC-16:30 | 18-DEC-10:00
BLD2PST |  | Source Energy
BLD2PST |  |  | Total Source Energy (GJ) | 169484.78 | 187414.78 | 162378.72 | 171396.83 | 149760.24 | 172507.11 | 141593.93 | 179502.82 | 146705.67 | 87553.12 | 168239.49 | 144280.61 | 158190.16 | 147568.11 | 152072.03 | 151376.84
BLD2PST |  |  | Total Source Energy (MJ/m2) | 7558.78 | 8358.43 | 7241.86 | 7644.05 | 6679.09 | 7693.57 | 6314.89 | 8005.57 | 6542.86 | 3904.74 | 7503.24 | 6434.71 | 7055.06 | 6581.33 | 6782.2 | 6751.19
BLD2PST |  | Water Consumption (m3)
BLD2PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Heat Rejection | 40269.52 | 34223.06 | 42996.58 | 28840.48 | 25275.24 | 36622.36 | 17491.89 | 25316.04 | 23972.31 | 16832.45 | 21198.75 | 19900.51 | 18792.58 | 15928.49 | 13573 | 9396.54
BLD2PST |  |  | Humidification | 9.66 | 117.34 | 478.61 | 305.12 | 121.12 | 919.32 | 80.89 | 485.63 | 885.04 | 251.83 | 588.07 | 921.98 | 711.45 | 920.13 | 895.16 | 1208.47
BLD2PST |  |  | Water Systems | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67
BLD2PST |  |  | Total Building | 44284.86 | 38346.07 | 47480.86 | 33151.27 | 29402.04 | 41547.35 | 21578.45 | 29807.35 | 28863.03 | 21089.95 | 25792.49 | 24828.16 | 23509.7 | 20854.29 | 18473.83 | 14610.68
BLD2PST |  | Emissions
BLD2PST |  |  | Carbon Equivalent (kg) | 3817560 | 4657080 | 4167190 | 4226360 | 1659860 | 4387710 | 1581110 | 3692080 | 4799350 | 1096910 | 6598810 | 4700900 | 4176860 | 4118540 | 3993810 | 3168820
BLD2PST |  |  | CO2 (kg) | 8949780 | 11772400 | 9922170 | 9744940 | 4485090 | 10508300 | 4279000 | 8449200 | 11296700 | 2744300 | 15388000 | 11075400 | 9801630 | 9719140 | 9391570 | 8107670
BLD2PST |  |  | NOX (kg) | 15309.7605 | 15206.3665 | 16256.2654 | 18088.5281 | 3874.9646 | 16761.8251 | 3701.4532 | 16066.3528 | 19322.9301 | 3864.5278 | 27282.21 | 18899.2271 | 17104.16 | 16629.8686 | 16301.7572 | 9717.0552
BLD2PST |  |  | SO2 (kg) | 56593.1267 | 63344.7726 | 52485.2049 | 45352.078 | 35254.9508 | 67932.4702 | 32823.0093 | 46400.1817 | 49133.5006 | 8780.912 | 79880.5605 | 47926.4724 | 26769.0477 | 28280.9504 | 25366.4046 | 49339.0262
BLD2PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2PST |  |  | Hg (kg) | 0.259 | 0.1793 | 0.1437 | 0.1669 | 0.0173 | 0.1286 | 0.0163 | 0.1884 | 0.1925 | 0.0357 | 0.2423 | 0.1879 | 0.1969 | 0.1975 | 0.1868 | 0.1694
BLD2PST |  |  | Water for Electricity (m3) | 7003.82 | 21606.7 | 387681 | 80665.9 | 212701 | 338781 | 198025 | 2885.63 | 51088.1 | 116017 | 18388.5 | 49832.8 | 17593.6 | 670831 | 16671.4 | 9901.38
BLD2NEW |  | Program
BLD2NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD2NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD2NEW |  |  | Weighting Factor | 2.212 | 26.2479 | 5.2507 | 25.6471 |  | 14.9424 | 2.1414 | 33.7424 | 1.2208 | 5.8045 | 44.5219 | 11.9724 | 12.1239 | 1.2983 | 1.8482 | 0.07226
BLD2NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD2NEW |  |  | Exterior walls
BLD2NEW | TypeWall |  | Construction Type | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall | MassWall
BLD2NEW | RvalWall |  | R-value (m2·K / W) | 2.377 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
BLD2NEW |  |  | Underground walls
BLD2NEW |  |  | Construction Type | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete | 8in concrete
BLD2NEW |  |  | R-value (m2·K / W) | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 0.30675 | 1.6313 | 1.6313
BLD2NEW |  |  | Roof
BLD2NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD2NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD2NEW |  |  | Window
BLD2NEW | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
BLD2NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
BLD2NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
BLD2NEW |  |  | Skylights/TDD
BLD2NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD2NEW |  |  | Foundation
BLD2NEW |  |  | Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
BLD2NEW |  |  | Construction | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab
BLD2NEW |  |  | R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
BLD2NEW |  | HVAC
BLD2NEW |  |  | HVAC Sizing
BLD2NEW |  |  | Air Conditioning (kW)
BLD2NEW | HVAC |  | COOLSYS1 CHILLER | 2964.08 | 2945.3231 | 2673.5664 | 2709.2499 | 2279.0616 | 2291.3469 | 2030.5039 | 2763.9099 | 1929.6802 | 2053.7548 | 2726.1701 | 1913.698 | 2633.709 | 1850.7698 | 2336.5893 | 1812.409
BLD2NEW |  |  | Heating (kW)
BLD2NEW | HEAT |  | HEATSYS1 BOILER | 2897.0791 | 3064.559 | 2942.8831 | 3133.4104 | 2845.4191 | 2899.1659 | 3054.0461 | 3290.0611 | 2766.7324 | 3068.5765 | 3444.8015 | 2926.4657 | 3531.9221 | 3225.4349 | 3559.1337 | 3876.5121
BLD2NEW |  |  | HVAC Efficiency
BLD2NEW | COP |  | Air Conditioning (COP) | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 6.1
BLD2NEW | EffHeat |  | Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
BLD2NEW |  |  | HVAC Control - Economizer
BLD2NEW |  |  | CAV_1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD2NEW |  |  | CAV_2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
BLD2NEW |  |  | VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD2NEW |  |  | VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
BLD2NEW | Fan |  | Fan Max Flow Rate (m3/s ) | 96.91 | 97.52 | 99.55 | 94.99 | 91.72 | 95.03 | 92.67 | 94.29 | 98.97 | 91.56 | 94.11 | 97.95 | 93.63 | 95.67 | 93.72 | 87.08
BLD2NEW |  |  | CAV_1_FAN | 15.94 | 16.05 | 16.68 | 15.85 | 15.49 | 16.15 | 17.4 | 15.76 | 16.15 | 15.58 | 15.76 | 16.04 | 15.71 | 15.87 | 16.13 | 15.27
BLD2NEW |  |  | CAV_2_FAN | 12.17 | 12.19 | 12.43 | 12.09 | 12 | 12.16 | 12.34 | 12.1 | 12.14 | 12.06 | 12.1 | 12.11 | 12.09 | 12.09 | 12.13 | 11.99
BLD2NEW |  |  | VAV_1_FAN | 26.15 | 26.13 | 25.51 | 24.77 | 23.68 | 23.56 | 22.51 | 24.5 | 26.18 | 22.81 | 24.39 | 25.94 | 24.26 | 24.8 | 23.64 | 20.72
BLD2NEW |  |  | VAV_2_FAN | 42.65 | 43.15 | 44.93 | 42.28 | 40.55 | 43.16 | 40.42 | 41.93 | 44.5 | 41.11 | 41.86 | 43.86 | 41.57 | 42.91 | 41.82 | 39.1
BLD2NEW |  | Utility Costs
BLD2NEW |  |  | Electric Utility Rates
BLD2NEW |  |  | Average Annual Rate ($/kWh) | 0.072379 | 0.091176 | 0.063016 | 0.095329 | 0.039164 | 0.083574 | 0.12197 | 0.0504 | 0.03695 | 0.063496 | 0.10031 | 0.036951 | 0.049093 | 0.067093 | 0.049678 | 0.08695
BLD2NEW |  |  | Total Cost ($/m2) | 33.13 | 42.01 | 28.34 | 42.29 | 16.13 | 35.3 | 48.5 | 22.23 | 14.2 | 24.98 | 41.26 | 13.91 | 19.38 | 24.57 | 18.6 | 28.79
BLD2NEW |  |  | Gas Utility Rates
BLD2NEW |  |  | Average Annual Rate ($/MJ) | 0.01145 | 0.0081771 | 0.0085579 | 0.010807 | 0.0084008 | 0.0081512 | 0.0084051 | 0.010099 | 0.0071886 | 0.0082862 | 0.0089236 | 0.0071859 | 0.0079809 | 0.0087156 | 0.007975 | 0.0041779
BLD2NEW |  |  | Total Cost ($/m2) | 6.21 | 5.08 | 4.83 | 6.92 | 5.28 | 4.56 | 6.17 | 7.28 | 3.75 | 5.95 | 6.74 | 4.13 | 6.46 | 5.88 | 6.87 | 4.67
BLD2NEW |  |  | Total Utility Costs
BLD2NEW |  |  | Cost Intensity ($/m2) | 39.34 | 47.09 | 33.18 | 49.21 | 21.41 | 39.86 | 54.67 | 29.51 | 17.95 | 30.93 | 48 | 18.03 | 25.84 | 30.44 | 25.47 | 33.46
BLD2NEW |  | Energy - End Uses
BLD2NEW |  |  | Electricity (kWh)
BLD2NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Cooling | 4772450 | 4818250 | 4404350 | 4423988.8889 | 3923005.5556 | 3674752.7778 | 3642350 | 4276100 | 2947044.4444 | 3517266.6667 | 3606750 | 2782902.7778 | 3215077.7778 | 2590652.7778 | 2725563.8889 | 1781552.7778
BLD2NEW |  |  | Interior Lighting | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667 | 1156866.6667
BLD2NEW |  |  | Exterior Lighting | 67375 | 67255.5556 | 67236.1111 | 67350 | 67336.1111 | 67272.2222 | 67200 | 67266.6667 | 67255.5556 | 67155.5556 | 67175 | 67186.1111 | 67230.5556 | 67147.2222 | 67130.5556 | 66727.7778
BLD2NEW |  |  | Interior Equipment | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444
BLD2NEW |  |  | Exterior Equipment | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667
BLD2NEW |  |  | Fans | 913508.3333 | 899788.8889 | 942386.1111 | 882950 | 864055.5556 | 904730.5556 | 921061.1111 | 874986.1111 | 906963.8889 | 860113.8889 | 873336.1111 | 894522.2222 | 871958.3333 | 880300 | 879591.6667 | 849652.7778
BLD2NEW |  |  | Pumps | 459938.8889 | 439066.6667 | 384608.3333 | 389580.5556 | 340055.5556 | 327325 | 292952.7778 | 385252.7778 | 274463.8889 | 285747.2222 | 364600 | 264405.5556 | 338772.2222 | 245911.1111 | 287213.8889 | 189305.5556
BLD2NEW |  |  | Heat Rejection | 317330.5556 | 311041.6667 | 285019.4444 | 275972.2222 | 243994.4444 | 239988.8889 | 217366.6667 | 263377.7778 | 188119.4444 | 216911.1111 | 229408.3333 | 172272.2222 | 198961.1111 | 156866.6667 | 162077.7778 | 102755.5556
BLD2NEW |  |  | Humidification | 5886.1111 | 72450 | 278541.6667 | 186638.8889 | 72575 | 534686.1111 | 56100 | 303711.1111 | 512277.7778 | 154552.7778 | 362886.1111 | 540063.8889 | 439483.3333 | 551572.2222 | 556811.1111 | 717725
BLD2NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Refrigeration | 57080.5556 | 54938.8889 | 55191.6667 | 52777.7778 | 53197.2222 | 53350 | 51575 | 51375 | 51313.8889 | 50413.8889 | 50416.6667 | 50138.8889 | 49975 | 49197.2222 | 48591.6667 | 47605.5556
BLD2NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total End Uses | 10261897.2222 | 10331119.4444 | 10085661.1111 | 9947583.3333 | 9232544.4444 | 9470433.3333 | 8916927.7778 | 9890397.2222 | 8615766.6667 | 8820491.6667 | 9222897.2222 | 8439819.4444 | 8849786.1111 | 8209975 | 8395305.5556 | 7423652.7778
BLD2NEW |  |  | Gas (MJ)
BLD2NEW |  |  | Heating | 10349520 | 12025510 | 10811550 | 12366180 | 12126470 | 10638320 | 14414250 | 14105820 | 9661030 | 14019470 | 14818960 | 10761160 | 15983570 | 12939920 | 17069920 | 22696010
BLD2NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Equipment | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420
BLD2NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Water Systems | 453040 | 543380 | 491440 | 630470 | 613600 | 554010 | 688100 | 698920 | 685940 | 734550 | 759010 | 755900 | 810910 | 820360 | 896550 | 1000220
BLD2NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total End Uses | 12160970 | 13927300 | 12661410 | 14355060 | 14098480 | 12550740 | 16460770 | 16163150 | 11705390 | 16112440 | 16936380 | 12875480 | 18152900 | 15118690 | 19324890 | 25054650
BLD2NEW |  |  | Purchased Cooling (MJ)
BLD2NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Purchased Heating (MJ)
BLD2NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total Building (MJ) | 49103800 | 51119330 | 48969790 | 50166370 | 47335640 | 46644300 | 48561710 | 51768580 | 42722140 | 47866210 | 50138820 | 43258820 | 50012120 | 44674600 | 49547990 | 51779800
BLD2NEW |  | Energy - End Use Intensities
BLD2NEW |  |  | Electricity (MJ/m2)
BLD2NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Cooling (elec) | 766.2401 | 773.5935 | 707.1399 | 710.293 | 629.8577 | 589.9995 | 584.7971 | 686.5487 | 473.1624 | 564.7143 | 579.0813 | 446.8086 | 516.1964 | 415.9419 | 437.6026 | 286.037
BLD2NEW |  |  | Interior Lighting (elec) | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406 | 185.7406
BLD2NEW |  |  | Exterior Lighting (elec) | 10.8174 | 10.7982 | 10.7951 | 10.8134 | 10.8111 | 10.8009 | 10.7893 | 10.8 | 10.7982 | 10.7822 | 10.7853 | 10.7871 | 10.7942 | 10.7808 | 10.7781 | 10.7135
BLD2NEW |  |  | Interior Equipment (elec) | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554
BLD2NEW |  |  | Exterior Equipment (elec) | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719
BLD2NEW |  |  | Fans (elec) | 146.6682 | 144.4655 | 151.3047 | 141.7619 | 138.7283 | 145.2589 | 147.8809 | 140.4833 | 145.6175 | 138.0955 | 140.2184 | 143.6199 | 139.9972 | 141.3365 | 141.2227 | 136.4159
BLD2NEW |  |  | Pumps (elec) | 73.8454 | 70.4943 | 61.7507 | 62.5491 | 54.5976 | 52.5536 | 47.035 | 61.8542 | 44.0665 | 45.8781 | 58.5383 | 42.4516 | 54.3915 | 39.4822 | 46.1136 | 30.3939
BLD2NEW |  |  | Heat Rejection (elec) | 50.949 | 49.9393 | 45.7613 | 44.3087 | 39.1745 | 38.5314 | 34.8993 | 42.2866 | 30.2035 | 34.8261 | 36.8326 | 27.6591 | 31.9442 | 25.1857 | 26.0224 | 16.4979
BLD2NEW |  |  | Humidification (elec) | 0.94504 | 11.6322 | 44.7212 | 29.9658 | 11.6523 | 85.8465 | 9.0071 | 48.7623 | 82.2487 | 24.8142 | 58.2631 | 86.7099 | 70.5612 | 88.5576 | 89.3987 | 115.2342
BLD2NEW |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Refrigeration (elec) | 9.1646 | 8.8207 | 8.8613 | 8.4737 | 8.5411 | 8.5656 | 8.2806 | 8.2485 | 8.2387 | 8.0942 | 8.0946 | 8.05 | 8.0237 | 7.8989 | 7.8016 | 7.6433
BLD2NEW |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total End Uses | 1647.5977 | 1658.7116 | 1619.3021 | 1597.133 | 1482.33 | 1520.5243 | 1431.6562 | 1587.9515 | 1383.3034 | 1416.173 | 1480.7811 | 1355.0542 | 1420.8763 | 1318.1515 | 1347.9073 | 1191.9037
BLD2NEW |  |  | Gas (MJ/m2)
BLD2NEW |  |  | Heating (gas) | 461.5739 | 536.3206 | 482.1797 | 551.514 | 540.8233 | 474.4539 | 642.855 | 629.0995 | 430.8682 | 625.2484 | 660.9045 | 479.9324 | 712.8445 | 577.102 | 761.2941 | 1012.2098
BLD2NEW |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Equipment (gas) | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836
BLD2NEW |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Water Systems (gas) | 20.2049 | 24.234 | 21.9175 | 28.1181 | 27.3657 | 24.7081 | 30.6883 | 31.1708 | 30.5919 | 32.7599 | 33.8508 | 33.7121 | 36.1654 | 36.5869 | 39.9849 | 44.6084
BLD2NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total End Uses | 542.362 | 621.1378 | 564.6809 | 640.2153 | 628.7721 | 559.7451 | 734.1269 | 720.8535 | 522.0437 | 718.5919 | 755.3384 | 574.2281 | 809.5935 | 674.2721 | 861.8626 | 1117.4017
BLD2NEW |  |  | Purchased Cooling (MJ/m2)
BLD2NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Purchased Heating (MJ/m2)
BLD2NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Total Building (MJ/m2) | 2189.9596 | 2279.8494 | 2183.983 | 2237.3487 | 2111.1022 | 2080.2694 | 2165.7832 | 2308.805 | 1905.3467 | 2134.7649 | 2236.12 | 1929.2818 | 2230.4694 | 1992.4236 | 2209.7699 | 2309.3054
BLD2NEW |  | Peak Energy Demand
BLD2NEW |  |  | Electricity Peak Demand (kW)
BLD2NEW |  |  | Jan | 1574.2947 | 1614.5356 | 1560.7585 | 1538.9076 | 1449.7626 | 1498.4729 | 1389.9012 | 1558.6221 | 1394.2211 | 1375.508 | 1475.0678 | 1395.7582 | 1265.2097 | 1309.4557 | 1282.6446 | 1298.7785
BLD2NEW |  |  | Feb | 1550.583 | 1580.2725 | 1579.1474 | 1527.0755 | 1428.9606 | 1490.2823 | 1366.583 | 1543.3626 | 1406.597 | 1389.9851 | 1491.1045 | 1385.4274 | 1306.3715 | 1371.2497 | 1423.6469 | 1306.0522
BLD2NEW |  |  | Mar | 1586.5502 | 1589.2287 | 1526.3716 | 1515.9579 | 1432.8722 | 1492.0359 | 1381.3599 | 1561.3734 | 1412.8239 | 1372.6631 | 1501.162 | 1394.5413 | 1511.5349 | 1350.1551 | 1364.442 | 1302.7858
BLD2NEW |  |  | Apr | 1552.7702 | 1567.4502 | 1538.0675 | 1498.4355 | 1406.009 | 1447.863 | 1350.5627 | 1542.027 | 1368.67 | 1362.8034 | 1564.4215 | 1367.2343 | 1519.1479 | 1350.0833 | 1451.4077 | 1325.4963
BLD2NEW |  |  | May | 1504.7611 | 1516.9277 | 1485.1106 | 1492.3605 | 1390.1131 | 1457.0666 | 1351.2075 | 1529.7922 | 1359.226 | 1343.1186 | 1535.2598 | 1354.7575 | 1503.9745 | 1330.4085 | 1457.9941 | 1328.0576
BLD2NEW |  |  | Jun | 1466.9577 | 1441.5114 | 1492.5688 | 1446.7381 | 1360.1959 | 1403.5143 | 1343.7663 | 1482.2348 | 1344.0522 | 1339.4389 | 1511.8443 | 1341.0394 | 1488.2603 | 1340.4454 | 1454.6015 | 1313.669
BLD2NEW |  |  | Jul | 1450.81 | 1442.5669 | 1432.2921 | 1429.9277 | 1306.9613 | 1405.1475 | 1334.3115 | 1455.9154 | 1309.7051 | 1327.8191 | 1443.5608 | 1282.3874 | 1454.6802 | 1275.8558 | 1414.4907 | 1270.679
BLD2NEW |  |  | Aug | 1449.2305 | 1486.411 | 1410.2111 | 1420.6284 | 1314.0057 | 1383.851 | 1324.393 | 1464.9134 | 1265.4601 | 1315.795 | 1485.3526 | 1279.4001 | 1438.9048 | 1304.4921 | 1422.6667 | 1287.0405
BLD2NEW |  |  | Sep | 1480.6105 | 1491.5693 | 1421.5269 | 1431.9326 | 1331.0404 | 1389.6019 | 1311.4113 | 1488.5592 | 1301.7454 | 1338.2808 | 1518.3667 | 1337.2579 | 1492.0179 | 1316.9184 | 1459.7821 | 1294.1804
BLD2NEW |  |  | Oct | 1489.5733 | 1527.6139 | 1520.5745 | 1508.0107 | 1392.4467 | 1441.4902 | 1325.9865 | 1542.2166 | 1387.716 | 1352.2406 | 1569.0013 | 1369.7997 | 1505.7531 | 1337.0855 | 1443.5748 | 1313.997
BLD2NEW |  |  | Nov | 1517.8634 | 1596.7267 | 1508.6343 | 1550.3487 | 1436.0742 | 1482.9868 | 1374.3038 | 1556.2758 | 1414.5823 | 1370.6521 | 1503.3975 | 1401.39 | 1524.9025 | 1352.7701 | 1473.164 | 1210.6918
BLD2NEW |  |  | Dec | 1548.2631 | 1596.2223 | 1562.2192 | 1545.3276 | 1475.9793 | 1493.0992 | 1411.1106 | 1535.2629 | 1386.9967 | 1352.588 | 1472.7788 | 1380.7012 | 1315.6968 | 1338.3557 | 1254.5216 | 1279.4891
BLD2NEW |  |  | Time of Peak Electrical Demand
BLD2NEW |  |  | Jan | 02-JAN-17:00 | 09-JAN-17:45 | 24-JAN-17:00 | 26-JAN-17:00 | 18-JAN-14:00 | 30-JAN-17:30 | 20-JAN-13:15 | 05-JAN-16:00 | 18-JAN-17:45 | 03-JAN-17:00 | 17-JAN-14:15 | 24-JAN-17:00 | 30-JAN-17:00 | 25-JAN-17:15 | 13-JAN-16:45 | 20-JAN-17:00
BLD2NEW |  |  | Feb | 10-FEB-17:00 | 08-FEB-15:15 | 21-FEB-14:00 | 22-FEB-17:00 | 27-FEB-10:45 | 06-FEB-17:45 | 23-FEB-17:00 | 28-FEB-17:00 | 15-FEB-17:45 | 21-FEB-17:00 | 28-FEB-11:45 | 07-FEB-17:00 | 17-FEB-16:15 | 03-FEB-17:45 | 28-FEB-17:00 | 28-FEB-16:15
BLD2NEW |  |  | Mar | 15-MAR-09:15 | 29-MAR-15:00 | 03-MAR-10:15 | 13-MAR-15:15 | 22-MAR-16:00 | 06-MAR-17:45 | 03-MAR-17:00 | 10-MAR-17:45 | 03-MAR-17:00 | 23-MAR-15:00 | 14-MAR-13:45 | 31-MAR-15:45 | 31-MAR-16:45 | 31-MAR-16:00 | 21-MAR-15:00 | 28-MAR-16:00
BLD2NEW |  |  | Apr | 06-APR-09:15 | 07-APR-09:00 | 20-APR-08:15 | 26-APR-09:00 | 11-APR-15:00 | 13-APR-09:15 | 21-APR-16:30 | 21-APR-16:00 | 11-APR-16:00 | 26-APR-16:00 | 27-APR-16:00 | 10-APR-10:45 | 13-APR-16:00 | 04-APR-16:00 | 27-APR-15:45 | 25-APR-16:00
BLD2NEW |  |  | May | 02-MAY-08:15 | 10-MAY-09:15 | 16-MAY-16:00 | 09-MAY-09:15 | 19-MAY-10:15 | 05-MAY-16:00 | 19-MAY-16:00 | 18-MAY-15:00 | 05-MAY-16:00 | 11-MAY-15:15 | 09-MAY-16:00 | 09-MAY-15:00 | 17-MAY-16:00 | 18-MAY-10:45 | 12-MAY-16:00 | 09-MAY-15:15
BLD2NEW |  |  | Jun | 02-JUN-16:00 | 05-JUN-16:00 | 19-JUN-10:45 | 12-JUN-09:15 | 01-JUN-08:00 | 14-JUN-16:00 | 02-JUN-16:00 | 20-JUN-10:00 | 26-JUN-16:00 | 08-JUN-10:45 | 23-JUN-15:15 | 15-JUN-16:00 | 14-JUN-10:45 | 01-JUN-15:00 | 23-JUN-16:00 | 02-JUN-10:45
BLD2NEW |  |  | Jul | 25-JUL-15:00 | 28-JUL-16:00 | 06-JUL-10:00 | 05-JUL-10:45 | 12-JUL-15:00 | 31-JUL-16:00 | 06-JUL-10:45 | 20-JUL-10:45 | 31-JUL-16:00 | 03-JUL-15:00 | 05-JUL-10:45 | 12-JUL-15:00 | 31-JUL-10:45 | 13-JUL-08:15 | 21-JUL-09:45 | 27-JUL-08:15
BLD2NEW |  |  | Aug | 11-AUG-15:00 | 09-AUG-10:45 | 16-AUG-10:00 | 30-AUG-08:15 | 09-AUG-16:00 | 15-AUG-10:00 | 03-AUG-09:15 | 23-AUG-09:15 | 29-AUG-16:00 | 10-AUG-09:15 | 07-AUG-08:15 | 28-AUG-16:00 | 11-AUG-08:00 | 31-AUG-09:30 | 31-AUG-16:00 | 28-AUG-16:00
BLD2NEW |  |  | Sep | 21-SEP-09:00 | 26-SEP-10:45 | 22-SEP-06:15 | 13-SEP-09:15 | 21-SEP-07:15 | 29-SEP-16:00 | 12-SEP-08:15 | 22-SEP-14:00 | 20-SEP-16:00 | 19-SEP-16:00 | 20-SEP-15:45 | 26-SEP-10:45 | 28-SEP-16:00 | 14-SEP-10:45 | 27-SEP-15:15 | 28-SEP-16:00
BLD2NEW |  |  | Oct | 24-OCT-08:15 | 16-OCT-09:15 | 16-OCT-08:15 | 23-OCT-09:15 | 30-OCT-07:15 | 30-OCT-16:00 | 24-OCT-09:15 | 17-OCT-16:00 | 26-OCT-16:00 | 16-OCT-16:00 | 26-OCT-16:00 | 17-OCT-15:15 | 19-OCT-15:15 | 17-OCT-15:15 | 19-OCT-15:15 | 03-OCT-16:00
BLD2NEW |  |  | Nov | 22-NOV-09:15 | 29-NOV-17:45 | 01-NOV-09:15 | 16-NOV-17:00 | 24-NOV-17:00 | 24-NOV-17:30 | 20-NOV-16:00 | 07-NOV-16:00 | 13-NOV-17:00 | 21-NOV-16:00 | 01-NOV-16:00 | 10-NOV-16:00 | 01-NOV-16:00 | 21-NOV-16:45 | 03-NOV-16:00 | 14-NOV-09:15
BLD2NEW |  |  | Dec | 01-DEC-17:00 | 22-DEC-17:30 | 27-DEC-17:45 | 27-DEC-17:45 | 08-DEC-16:00 | 14-DEC-16:00 | 29-DEC-16:00 | 08-DEC-16:00 | 05-DEC-16:00 | 07-DEC-17:00 | 12-DEC-11:45 | 29-DEC-16:00 | 01-DEC-13:00 | 01-DEC-16:45 | 01-DEC-16:30 | 18-DEC-10:00
BLD2NEW |  | Source Energy
BLD2NEW |  |  | Total Source Energy (GJ) | 135819.14 | 150290.07 | 128669.67 | 136144.96 | 118264.56 | 135658.08 | 117327.58 | 144975.17 | 115695.88 | 72909.84 | 136230.37 | 114871.97 | 129323.13 | 119245.94 | 124979.57 | 122821.91
BLD2NEW |  |  | Total Source Energy (MJ/m2) | 6057.34 | 6702.72 | 5738.48 | 6071.87 | 5274.43 | 6050.16 | 5232.64 | 6465.69 | 5159.87 | 3251.68 | 6075.68 | 5123.13 | 5767.63 | 5318.2 | 5573.91 | 5477.68
BLD2NEW |  | Water Consumption (m3)
BLD2NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Heat Rejection | 34657.88 | 29428.92 | 36542.6 | 24244.08 | 20656.9 | 30689.14 | 15160.33 | 21645.84 | 19997.21 | 14151.34 | 18028.26 | 16689.5 | 16029.34 | 13485.89 | 11506.87 | 7622.6
BLD2NEW |  |  | Humidification | 7.88 | 97.02 | 373.02 | 249.95 | 97.19 | 716.05 | 75.13 | 406.73 | 686.04 | 206.98 | 485.98 | 723.25 | 588.56 | 738.66 | 745.68 | 961.18
BLD2NEW |  |  | Water Systems | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67 | 4005.67
BLD2NEW |  |  | Total Building | 38671.44 | 33531.62 | 40921.3 | 28499.7 | 24759.76 | 35410.86 | 19241.12 | 26058.24 | 24688.93 | 18363.99 | 22519.9 | 21418.42 | 20623.56 | 18230.23 | 16258.22 | 12589.45
BLD2NEW |  | Emissions
BLD2NEW |  |  | Carbon Equivalent (kg) | 3033620 | 3697210 | 3272930 | 3323080 | 1333200 | 3420460 | 1338920 | 2960440 | 3730600 | 932983.5274 | 5222590 | 3679830 | 3356570 | 3272860 | 3222130 | 2540720
BLD2NEW |  |  | CO2 (kg) | 7150300 | 9372760 | 7819670 | 7702450 | 3615200 | 8219260 | 3639790 | 6827370 | 8810680 | 2365540 | 12227700 | 8704170 | 7929310 | 7765830 | 7631730 | 6538130
BLD2NEW |  |  | NOX (kg) | 12068.1274 | 12024.6463 | 12700.4682 | 14108.2334 | 3132.0585 | 13000.2973 | 3159.5214 | 12731.5014 | 14942.338 | 3214.1442 | 21459.646 | 14703.8447 | 13602.3229 | 13101.994 | 13003.3065 | 7740.7641
BLD2NEW |  |  | SO2 (kg) | 43928.2801 | 49283.1742 | 40559.8554 | 34919.8683 | 26869.3763 | 52098.3264 | 25951.6041 | 36108.2363 | 37626.4621 | 6821.8516 | 62159.497 | 36858.4505 | 20891.7743 | 21925.6666 | 19819.4422 | 37796.0772
BLD2NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD2NEW |  |  | Hg (kg) | 0.2015 | 0.14 | 0.1113 | 0.1289 | 0.0136 | 0.0989 | 0.0134 | 0.1472 | 0.1478 | 0.0282 | 0.1891 | 0.1449 | 0.1542 | 0.1536 | 0.1466 | 0.1305
BLD2NEW |  |  | Water for Electricity (m3) | 5436.32 | 16809.9 | 299589 | 62108.7 | 162103 | 259812 | 156561 | 2245.49 | 39122.5 | 90117.2 | 14308.8 | 38323.5 | 13729.9 | 520054 | 13024.8 | 7584.6

## Picture
DOE Commercial Building Benchmark - Hospital
Second Floor
Third Floor
Forth Floor
Fifth Floor

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Kitchen_Exhaust_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 73 | 3806.43
[5 empty] | Sats | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | ADMIN_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 93.6 | 4880.57
[5 empty] | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
[5 empty] | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
|  | ADMIN_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 73.1 | 3811.64
[5 empty] | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
[5 empty] | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
|  | ADMIN_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
[5 empty] | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
[5 empty] | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
|  | BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 76.56 | 3992.06
[5 empty] | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
[5 empty] | Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
|  | BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 58.5 | 3050.36
[5 empty] | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
[5 empty] | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
SchEquip | WD | CRITICAL_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6 | 130.2 | 6789
| Sat |  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
| Sun |  |  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
SchLight | WD | CRITICAL_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18 | 108 | 5631.43
| Sat |  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
| Sun |  |  |  | Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
SchOcc | WD | CRITICAL_OCC_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1 | 102.6 | 5349.86
| Sat |  |  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
| Sun |  |  |  | Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  | INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 36 | 1877.14
[5 empty] | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
[5 empty] | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
[5 empty] | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  | Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 17.7 | 922.93
[5 empty] | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
[5 empty] | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
SchGas | WD | Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 18.25 | 951.61
| Sat |  |  |  |  | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 18.25 | 951.61
[5 empty] | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
[5 empty] | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  | Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | ADMIN_CLGSETP_SCH | Temperature | Through 12/31 | WD | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3395.6 | 177056.29
[5 empty] | SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6
[5 empty] | WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
[5 empty] | Sats | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
[5 empty] | Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
|  | ADMIN_HTGSETP_SCH | Temperature | Through 12/31 | WD | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 2839.6 | 148064.86
[5 empty] | SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6
[5 empty] | WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
[5 empty] | Sats | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
[5 empty] | Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
|  | Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | WD | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668 | 4028 | 210031.43
[5 empty] | SummerDesign | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668
[5 empty] | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
[5 empty] | Sats | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
[5 empty] | Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  | Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6 | 2494.6 | 130075.57
[5 empty] | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6
[5 empty] | WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
[5 empty] | Sats | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
[5 empty] | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
SetCool | All | CRITICAL_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 532.8 | 3729.6 | 194472
SetHeat | All | CRITICAL_HTGSETP_SCH | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
|  | OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
|  | OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
|  | CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
|  | Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
|  | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
|  | HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | CAV_OAminFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
|  | VAV_OAminFracSchedule | Fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  | CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
|  | HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
|  | PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
|  | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
|  | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
|  | Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
[5 empty] | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
|  | Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
|  | BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 57.4 | 2993
[5 empty] | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
SchSWH | WD | BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
| Sat |  |  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
| Sun |  |  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
|  | Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
|  | Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600