## 1
1 | Building Summary Midrise Apartment pre-1980 construction
UWG |  |  | Value | Value | Value
areaFloor |  | Total Floor Area (m2) | 3135 | 3135 | 3135
nFloor |  | Number of Floors | 4 | 4 | 4
glazing |  | Total | 0.52 | 0.52 | 0.52
hCeiling |  | Floor to Ceiling Height (m) | 3.7 | 3.7 | 3.7
areaWall |  | Gross Dimensions - Total Area (m2) | 1542 | 1542 | 1542
ver2hor |  | Wall to Skin Ratio | 0.66304 | 0.66304 | 0.66304
areaRoof |  | Gross Dimensions - Total Area (m2) | 783.66 | 783.66 | 783.66
areaWindow |  | Total Area (m2) | 231.09 | 231.09 | 231.09

## 2
2 |  | Zone Summary
Building | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD6PRE | Total | Total Conditioned Zones |  |  | 3134.64 | 9553.48 |  | 1542.0014 | 231.12 |  | 160.7508 | 10 | 13 | 0 | 408.27 | 0.25 | 0.5 |  |  | 0.33
BLD6PST | Total | Total Conditioned Zones |  |  | 3134.64 | 9553.48 |  | 1542.0014 | 231.12 |  | 160.7508 | 10 | 13 | 0 | 408.27 | 0.25 | 0.5 |  |  | 0.33
BLD6NEW | Total | Total Conditioned Zones |  |  | 3134.64 | 9553.48 |  | 1542.0014 | 231.12 |  | 160.7508 | 10 | 13 | 0 | 408.27 | 0.25 | 0.5 |  |  | 0.33
19.5

## 3
3 | UWG | Location Summary
UWG | City |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD6PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD6PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD6PRE | RvalWall |  | R-value (m2·K / W) | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
BLD6PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD6PRE | RvalRoof |  | R-value (m2·K / W) | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD6PRE | Uwindow |  | U-Factor (W / m2·K) | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41
BLD6PRE | SHGC |  | SHGC | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
BLD6PRE | HVAC |  | Air Conditioning (kW) | 218.2419 | 234.6495 | 264.4851 | 252.1758 | 155.9296 | 223.9576 | 140.4045 | 257.8045 | 193.7969 | 173.1503 | 310.8604 | 254.9565 | 349.6901 | 271.7845 | 371.2556 | 344.8839 | 73.3652
BLD6PRE | HEAT |  | Heating (kW) | 106.4603 | 211.5329 | 157.5713 | 256.1308 | 123.8699 | 197.4416 | 157.155 | 285.0362 | 234.9752 | 219.7707 | 352.757 | 295.5391 | 395.1899 | 373.6132 | 414.5649 | 554.7994
BLD6PRE | COP |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
BLD6PRE | EffHeat |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 8.84 | 9.55 | 11.44 | 10.46 | 6.94 | 10.87 | 7.5 | 10.6 | 10.55 | 9.03 | 12.76 | 12.84 | 14.4 | 15.36 | 15.42 | 20.04
BLD6PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD6PST | RvalWall |  | R-value (m2·K / W) | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
BLD6PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD6PST | RvalRoof |  | R-value (m2·K / W) | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD6PST | Uwindow |  | U-Factor (W / m2·K) | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41
BLD6PST | SHGC |  | SHGC | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
BLD6PST | HVAC |  | Air Conditioning (kW) | 252.209 | 186.5944 | 224.877 | 202.4762 | 146.0699 | 179.3843 | 110.8242 | 208.9728 | 169.4711 | 142.5729 | 277.4041 | 228.9291 | 306.8673 | 243.3185 | 325.3708 | 302.8177
BLD6PST | HEAT |  | Heating (kW) | 132.396 | 192.1749 | 152.1751 | 222.8413 | 122.7435 | 177.7299 | 137.6554 | 244.542 | 202.1118 | 192.4166 | 321.5583 | 263.2391 | 355.212 | 337.5726 | 370.9174 | 496.7395
BLD6PST | COP |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
BLD6PST | EffHeat |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST | Fan |  | Fan Max Flow Rate (m3/s ) | 10.22 | 7.55 | 9.38 | 8.28 | 6.39 | 8.23 | 5.74 | 8.56 | 8.66 | 7.13 | 11.36 | 11.16 | 12.56 | 13.52 | 13.43 | 17.47
BLD6NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD6NEW | RvalWall |  | R-value (m2·K / W) | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526 | 0.39526
BLD6NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD6NEW | RvalRoof |  | R-value (m2·K / W) | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36 | 1.36
BLD6NEW | Uwindow |  | U-Factor (W / m2·K) | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41 | 3.41
BLD6NEW | SHGC |  | SHGC | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57 | 0.57
BLD6NEW | HVAC |  | Air Conditioning (kW) | 129.8738 | 134.1984 | 147.1211 | 126.47 | 91.1213 | 118.5573 | 96.5357 | 117.8185 | 89.0509 | 84.7196 | 134.6626 | 105.4876 | 147.9093 | 112.5806 | 150.5374 | 125.9769
BLD6NEW | HEAT |  | Heating (kW) | 60.7714 | 110.5184 | 84.0321 | 117.7647 | 63.7219 | 92.2588 | 79.6706 | 133.0672 | 109.439 | 103.2778 | 177.736 | 149.5417 | 202.6672 | 193.5932 | 214.8436 | 264.2636
BLD6NEW | COP |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
BLD6NEW | EffHeat |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW | Fan (m3/s ) |  | Fan Max Flow Rate (m3/s ) | 5.24 | 5.45 | 6.26 | 5.19 | 3.97 | 5.46 | 5.18 | 4.77 | 4.82 | 4.24 | 5.54 | 5.57 | 6.08 | 6.53 | 6.51 | 7.2
2.53

## 4
4 | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
SchEquip | WD | APT_EQP_SCH | Fraction | Through 12/31 | All | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3 | 15.79 | 110.53 | 5763.35
| Sat |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3
| Sun |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3
SchLight | WD | APT_LIGHT_SCH | Fraction | Through 12/31 | All | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3 | 7.88 | 55.16 | 2876.2
| Sat |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3
| Sun |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.9 | 0.9 | 0.9 | 0.7 | 0.3
SchOcc | WD | APT_OCC_SCH | Fraction | Through 12/31 | All | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 16.42 | 114.94 | 5993.3
| Sat |  |  |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| Sun |  |  |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
SetCool | WD | APT_CLGSETP_SCH | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 573.6 | 4015.2 | 209364
| Sat |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
| Sun |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
SetHeat | WD | APT_HTGSETP_SCH | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 506.4 | 3544.8 | 184836
| Sat |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
| Sun |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
SchGas | WD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sat |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchSWH | WD | APT_DHW_SCH | Fraction | Through 12/31 | All | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
| Sat |  |  |  |  | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
| Sun |  |  |  |  | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29

## BuildingSummary
1 | Building Summary Midrise Apartment pre-1980 construction
UWG |  |  | Value | Value | Value
Program
|  | Building Name | Midrise Apartment Reference Building pre-1980 construction | Midrise Apartment Reference Building post-1980 construction | Midrise Apartment Reference Building new construction 90.1-2004
|  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity
|  | Principal Building Activity | Multifamily residential | Multifamily residential | Multifamily residential
Form
areaFloor |  | Total Floor Area (m2) | 3135 | 3135 | 3135
|  | Building Shape | Rectangle | Rectangle | Rectangle
|  | Aspect Ratio | 2.74 | 2.74 | 2.74
nFloor |  | Number of Floors | 4 | 4 | 4
Window Fraction (Window to Wall Ratio)
|  | South | 0.1474 | 0.1474 | 0.1474
|  | East | 0.162 | 0.162 | 0.162
|  | North | 0.1474 | 0.1474 | 0.1474
|  | West | 0.1513 | 0.1513 | 0.1513
glazing |  | Total | 0.1499 | 0.1499 | 0.1499
|  | Skylight/TDD Percentage | 0 | 0 | 0
|  | Shading Geometry | None | None | None
|  | Azimuth | 0 | 0 | 0
|  | Thermal Zoning | 8 apartments with central corridor on each floor, office on first floor, 2x mulitplier on middle floor | 8 apartments with central corridor on each floor, office on first floor, 2x mulitplier on middle floor | 8 apartments with central corridor on each floor, office on first floor, 2x mulitplier on middle floor
hCeiling |  | Floor to Ceiling Height (m) | 3.05 | 3.05 | 3.05
|  | Floor to Floor Height (m) | 3.05 | 3.05 | 3.05
|  | Roof type | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck | Built-up flat roof, insulation entirely above deck
Fabric
Exterior walls
|  | Construction Type | Steel frame | Steel frame | Steel frame
areaWall |  | Gross Dimensions - Total Area (m2) | 1542 | 1542 | 1542
|  | Net Dimensions - Total Area (m2) | 1310.88 | 1310.88 | 1310.88
ver2hor |  | Wall to Skin Ratio | 0.66304 | 0.66304 | 0.66304
Roof
|  | Construction Type | IEAD | IEAD | IEAD
areaRoof |  | Gross Dimensions - Total Area (m2) | 783.66 | 783.66 | 783.66
|  | Net Dimensions - Total Area (m2) | 783.66 | 783.66 | 783.66
|  | Roof to Skin Ratio | 0.33696 | 0.33696 | 0.33696
Window Dimensions (m2)
|  | South | 83.23 | 83.23 | 83.23
|  | East | 33.42 | 33.42 | 33.42
|  | North | 83.23 | 83.23 | 83.23
|  | West | 31.21 | 31.21 | 31.21
areaWindow |  | Total Area (m2) | 231.09 | 231.09 | 231.09
|  | Operable area (m2) | 0 | 0 | 0
Skylights/TDD
|  | Dimensions - Total Area (m2) | 0 | 0 | 0
|  | Operable area (m2) | 0 | 0 | 0
Foundation
|  | Foundation Type | Mass Floor | Mass Floor | Mass Floor
|  | Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
|  | Dimensions - Total Area (m2) | 783.66 | 783.66 | 783.66
Interior Partitions
|  | Construction | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board | 2x4 steel-frame with gypsum board
|  | Dimensions - Total Area (m2) | 1686.92 | 1686.92 | 1686.92
Internal Mass
|  | Construction | 15 cm wood | 15 cm wood | 15 cm wood
|  | Dimensions - Total Area (m2) | 6269.18 | 6269.18 | 6269.18
|  | Thermal diffusivity (m2/s) | 1.84e-07 | 1.84e-07 | 1.84e-07
Air Barrier System
|  | Infiltration (ACH) | 0.91798 | 0.91798 | 0.24479
HVAC
System Type
|  | Heating Type | Gas furnace | Gas furnace | Gas furnace
|  | Cooling Type | Split system DX | Split system DX | Split system DX
|  | Fan Control | CAV | CAV | CAV
Service Water Heating
|  | SWH Type | gas water heater | gas water heater | gas water heater
|  | Fuel | gas | gas | gas
|  | Thermal Efficiency (%) | 80 | 78 | 80
|  | Temperature Setpoint (ºC ) | 60 | 60 | 60
|  | Water Consumption (m3 ) | 1875.51 | 1875.51 | 1875.51

## ZoneSummary
2 |  | Zone Summary
Building | UWG | Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
BLD6PRE |  | G SW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | G NW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | OFFICE | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 44.12 | 2.0002 | 21.9987 | 12.9 |  |  |  |  | 20.0023 |  | 0.88802
BLD6PRE |  | G NE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | G N1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | G N2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | G S1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | G S2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | M SW APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | M NW APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | M SE APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | M NE APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | M N1 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | M N2 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | M S1 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | M S2 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | T SW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | T NW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | T SE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | T NE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PRE |  | T N1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | T N2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | T S1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | T S2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PRE |  | T CORRIDOR | No | 1 | 77.66 | 236.69 | 3.0478 | 10.22 | 2.23 |  |  | 9.9176 |  |  |  |  | 0.25 | 19.415 |  | 1.5154
BLD6PRE |  | G CORRIDOR | No | 1 | 77.66 | 236.69 | 3.0478 | 10.22 | 4.43 |  |  | 9.9176 |  |  |  |  | 0.25 | 19.415 |  | 0.17623
BLD6PRE |  | M CORRIDOR | No | 2 | 77.66 | 236.69 | 3.0478 | 10.22 | 2.23 |  |  | 9.9176 |  |  |  |  | 0.25 | 19.415 |  | 0.17623
BLD6PRE | Total | Total Conditioned Zones |  |  | 3134.64 | 9553.48 |  | 1542.0014 | 231.12 |  | 79.5002 | 4.9841 | 5.0603 | 0 | 408.27 |  | 0.45121 | 1414.3944 |  | 0.6413
BLD6PST |  | G SW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | G NW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | OFFICE | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 44.12 | 2.0002 | 21.9987 | 12.9 |  |  |  |  | 20.0023 |  | 0.88802
BLD6PST |  | G NE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | G N1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | G N2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | G S1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | G S2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | M SW APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | M NW APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | M SE APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | M NE APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | M N1 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | M N2 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | M S1 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | M S2 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | T SW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | T NW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | T SE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | T NE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.88802
BLD6PST |  | T N1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | T N2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | T S1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | T S2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.53567
BLD6PST |  | T CORRIDOR | No | 1 | 77.66 | 236.69 | 3.0478 | 10.22 | 2.23 |  |  | 9.9176 |  |  |  |  | 0.25 | 19.415 |  | 1.5154
BLD6PST |  | G CORRIDOR | No | 1 | 77.66 | 236.69 | 3.0478 | 10.22 | 4.43 |  |  | 9.9176 |  |  |  |  | 0.25 | 19.415 |  | 0.17623
BLD6PST |  | M CORRIDOR | No | 2 | 77.66 | 236.69 | 3.0478 | 10.22 | 2.23 |  |  | 9.9176 |  |  |  |  | 0.25 | 19.415 |  | 0.17623
BLD6PST | Total | Total Conditioned Zones |  |  | 3134.64 | 9553.48 |  | 1542.0014 | 231.12 |  | 79.5002 | 4.9841 | 5.0603 | 0 | 408.27 |  | 0.45121 | 1414.3944 |  | 0.6413
BLD6NEW |  | G SW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | G NW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | OFFICE | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 44.12 | 2.0002 | 10.76 | 12.9 |  |  |  |  | 20.0023 |  | 0.23681
BLD6NEW |  | G NE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | G N1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | G N2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | G S1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | G S2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | M SW APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | M NW APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | M SE APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | M NE APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | M N1 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | M N2 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | M S1 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | M S2 APARTMENT | Yes | 2 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | T SW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | T NW APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | T SE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | T NE APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 58.5201 | 8.55 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.23681
BLD6NEW |  | T N1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | T N2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | T S1 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | T S2 APARTMENT | Yes | 1 | 88.25 | 268.96 | 3.0477 | 35.3 | 5.2 | 35.3 | 2.5 | 3.875 | 5.382 |  | 13.17 |  |  | 42.4752 |  | 0.14284
BLD6NEW |  | T CORRIDOR | No | 1 | 77.66 | 236.69 | 3.0478 | 10.22 | 2.23 |  |  | 5.382 |  |  |  |  | 0.25 | 19.415 |  | 0.4041
BLD6NEW |  | G CORRIDOR | No | 1 | 77.66 | 236.69 | 3.0478 | 10.22 | 4.43 |  |  | 5.382 |  |  |  |  | 0.25 | 19.415 |  | 0.046994
BLD6NEW |  | M CORRIDOR | No | 2 | 77.66 | 236.69 | 3.0478 | 10.22 | 2.23 |  |  | 5.382 |  |  |  |  | 0.25 | 19.415 |  | 0.046994
BLD6NEW | Total | Total Conditioned Zones |  |  | 3134.64 | 9553.48 |  | 1542.0014 | 231.12 |  | 79.5002 | 4.2182 | 5.0603 | 0 | 408.27 |  | 0.45121 | 1414.3944 |  | 0.17101

## LocationSummary
3 | UWG | Location Summary
UWG | City |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD6PRE |  | Program
BLD6PRE | Zone |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD6PRE |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD6PRE |  |  | Weighting Factor
BLD6PRE |  | Fabric
BLD6PRE |  |  | Exterior walls
BLD6PRE | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD6PRE | RvalWall |  | R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
BLD6PRE |  |  | Roof
BLD6PRE | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD6PRE | RvalRoof |  | R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
BLD6PRE |  |  | Window
BLD6PRE | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
BLD6PRE | SHGC |  | SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
BLD6PRE |  |  | Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
BLD6PRE |  |  | Foundation
BLD6PRE |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD6PRE |  |  | Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
BLD6PRE |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD6PRE |  | HVAC
BLD6PRE |  |  | HVAC Sizing
BLD6PRE | HVAC |  | Air Conditioning (kW) | 218.2419 | 234.6495 | 264.4851 | 252.1758 | 155.9296 | 223.9576 | 140.4045 | 257.8045 | 193.7969 | 173.1503 | 310.8604 | 254.9565 | 349.6901 | 271.7845 | 371.2556 | 344.8839
BLD6PRE |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 6.6019 | 6.9666 | 7.3647 | 6.9603 | 5.0519 | 6.1609 | 4.0662 | 6.9095 | 5.3863 | 4.4538 | 8.5955 | 7.1926 | 9.7877 | 7.6587 | 10.4914 | 9.5418
BLD6PRE |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_COOLCOIL | 16.791 | 17.2424 | 18.1206 | 16.6405 | 10.4229 | 15.5133 | 7.6091 | 15.0823 | 10.4936 | 9.0823 | 17.506 | 13.3574 | 19.8184 | 14.6287 | 20.6168 | 18.5727
BLD6PRE |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_COOLCOIL | 11.5552 | 12.5383 | 15.5088 | 13.4461 | 9.9595 | 13.2503 | 9.7979 | 14.1563 | 10.9054 | 10.6455 | 17.5018 | 14.4519 | 19.8432 | 15.4803 | 21.2065 | 19.1229
BLD6PRE |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_COOLCOIL | 11.8222 | 11.8349 | 14.211 | 13.4464 | 7.3471 | 11.3559 | 5.9966 | 14.1631 | 10.9081 | 8.7821 | 17.5113 | 15.1253 | 19.8322 | 16.1035 | 21.1998 | 19.865
BLD6PRE |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_COOLCOIL | 8.9057 | 8.9722 | 10.607 | 8.893 | 5.142 | 8.9657 | 3.4327 | 8.3419 | 6.3114 | 5.1091 | 10.3833 | 8.2898 | 11.8082 | 8.927 | 12.6451 | 10.8696
BLD6PRE |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_COOLCOIL | 8.808 | 8.8741 | 10.5327 | 8.7934 | 5.024 | 8.8912 | 3.4372 | 8.3422 | 6.3583 | 5.1216 | 10.3834 | 8.3058 | 11.8085 | 8.9324 | 12.6454 | 10.8696
BLD6PRE |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_COOLCOIL | 7.1598 | 8.4366 | 11.2045 | 9.2446 | 7.9376 | 9.9179 | 8.6476 | 9.4615 | 6.5758 | 8.8425 | 10.3757 | 8.6955 | 11.8222 | 9.4197 | 12.6553 | 11.5672
BLD6PRE |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_COOLCOIL | 7.1391 | 8.4555 | 11.2251 | 9.266 | 7.9533 | 9.9282 | 8.6525 | 9.48 | 6.573 | 8.8536 | 10.3758 | 8.7015 | 11.8225 | 9.431 | 12.6555 | 11.5643
BLD6PRE |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_COOLCOIL | 16.5455 | 18.0055 | 18.8275 | 16.8536 | 11.1793 | 16.0725 | 9.5738 | 15.8449 | 10.8109 | 10.5801 | 19.5411 | 14.4535 | 21.8661 | 15.7135 | 22.3855 | 20.8595
BLD6PRE |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_COOLCOIL | 13.4469 | 14.2037 | 15.0925 | 14.4291 | 8.0305 | 12.5115 | 6.7565 | 15.637 | 11.209 | 9.3577 | 19.5572 | 15.1739 | 21.8796 | 16.1998 | 23.5039 | 21.0467
BLD6PRE |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_COOLCOIL | 10.2311 | 11.8707 | 13.9624 | 14.581 | 7.5996 | 11.4886 | 6.6801 | 15.6268 | 11.7427 | 9.3482 | 19.5382 | 15.9058 | 21.8681 | 16.8035 | 23.4852 | 21.4561
BLD6PRE |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_COOLCOIL | 7.2748 | 7.3972 | 7.4709 | 7.1949 | 4.3434 | 6.1438 | 3.0087 | 6.8921 | 5.316 | 4.341 | 8.5777 | 7.2391 | 9.7546 | 7.6723 | 10.4578 | 9.2652
BLD6PRE |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_COOLCOIL | 10.1351 | 11.8709 | 13.1575 | 14.6008 | 6.951 | 10.629 | 7.0772 | 15.6392 | 11.9459 | 9.7853 | 19.5543 | 16.2071 | 21.8817 | 17.0506 | 23.5038 | 21.361
BLD6PRE |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_COOLCOIL | 8.9407 | 9.6735 | 11.1622 | 11.8622 | 5.7222 | 9.0309 | 5.857 | 12.7483 | 9.7161 | 8.0445 | 16.0043 | 13.273 | 17.8801 | 13.8665 | 19.2362 | 17.1542
BLD6PRE |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_COOLCOIL | 8.8838 | 9.6735 | 11.151 | 11.8621 | 5.7259 | 9.0141 | 5.8581 | 12.7483 | 9.7277 | 8.0488 | 16.0042 | 13.3141 | 17.8802 | 13.8722 | 19.2362 | 17.3014
BLD6PRE |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_COOLCOIL | 8.619 | 9.9166 | 11.8998 | 11.8409 | 6.6992 | 9.8404 | 5.7281 | 12.7355 | 9.7151 | 7.6585 | 15.989 | 13.2034 | 17.8677 | 13.8415 | 19.2189 | 17.7802
BLD6PRE |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_COOLCOIL | 8.6082 | 9.9102 | 11.9114 | 11.8407 | 6.7006 | 9.8367 | 5.7288 | 12.7355 | 9.7139 | 7.6586 | 15.9889 | 13.254 | 17.8677 | 13.8392 | 19.2189 | 17.7919
BLD6PRE |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_COOLCOIL | 8.6584 | 8.7886 | 8.6128 | 8.5094 | 6.4015 | 7.3949 | 5.3294 | 8.5101 | 6.6379 | 6.0298 | 10.5125 | 8.1267 | 11.3812 | 8.9101 | 11.5482 | 11.0253
BLD6PRE |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_COOLCOIL | 5.0689 | 4.9866 | 5.4075 | 6.4492 | 2.9614 | 5.0278 | 3.1486 | 6.9016 | 5.8724 | 4.6561 | 8.5844 | 8.3958 | 9.7638 | 8.7742 | 10.467 | 9.865
BLD6PRE |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_COOLCOIL | 3.6628 | 3.618 | 3.6345 | 3.8407 | 1.7888 | 3.2239 | 1.894 | 4.1383 | 3.5864 | 2.7401 | 5.1759 | 4.5942 | 5.9155 | 4.7105 | 6.3606 | 8.3462
BLD6PRE |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_COOLCOIL | 3.6175 | 3.5732 | 3.5916 | 3.8408 | 1.7209 | 3.2342 | 1.909 | 4.1385 | 3.594 | 2.7454 | 5.1761 | 4.6009 | 5.9156 | 4.8982 | 6.3607 | 8.3462
BLD6PRE |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_COOLCOIL | 2.8934 | 3.4289 | 3.9029 | 3.8732 | 3.2564 | 3.6361 | 2.6913 | 4.1573 | 3.8403 | 3.044 | 5.1963 | 5.1303 | 5.9514 | 5.3871 | 6.3971 | 6.3837
BLD6PRE |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_COOLCOIL | 3.0286 | 3.5619 | 4.041 | 4.0048 | 3.3491 | 3.7311 | 2.7749 | 4.2862 | 3.9325 | 3.136 | 5.3312 | 5.2535 | 6.0903 | 5.4622 | 6.5405 | 6.4638
BLD6PRE |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_COOLCOIL | 19.8444 | 20.8501 | 21.8851 | 19.9021 | 14.6614 | 19.1592 | 14.7492 | 19.1279 | 12.9243 | 15.0858 | 17.4964 | 12.7114 | 19.3836 | 14.2018 | 19.2191 | 18.4644
BLD6PRE | HEAT |  | Heating (kW) | 106.4603 | 211.5329 | 157.5713 | 256.1308 | 123.8699 | 197.4416 | 157.155 | 285.0362 | 234.9752 | 219.7707 | 352.757 | 295.5391 | 395.1899 | 373.6132 | 414.5649 | 554.7994
BLD6PRE |  |  | T CORRIDOR UNIT HEATER COIL | 0 | 2.0407 | 0.53407 | 3.2189 | 0 | 1.6102 | 0.50249 | 4.0484 | 2.8116 | 2.2013 | 6.0223 | 4.616 | 7.1219 | 6.6712 | 7.7604 | 11.9673
BLD6PRE |  |  | G CORRIDOR UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | M CORRIDOR UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 2.6249 | 5.8061 | 4.5069 | 7.1516 | 3.4715 | 5.7 | 4.4085 | 7.973 | 6.685 | 6.1822 | 9.8413 | 8.3065 | 11.1013 | 10.539 | 11.6317 | 15.5547
BLD6PRE |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_HEATCOIL | 6.2397 | 12.1022 | 8.847 | 14.7444 | 6.9812 | 11.1717 | 8.8687 | 16.248 | 13.3533 | 12.4921 | 19.9664 | 16.7047 | 22.4197 | 21.1512 | 23.4432 | 31.0136
BLD6PRE |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_HEATCOIL | 6.2429 | 12.1215 | 8.8184 | 14.7468 | 6.9729 | 11.1601 | 8.8418 | 16.2552 | 13.3717 | 12.4918 | 19.9627 | 16.6588 | 22.4419 | 21.1898 | 23.4592 | 31.017
BLD6PRE |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_HEATCOIL | 6.2418 | 12.1022 | 8.8374 | 14.7471 | 6.9758 | 11.1845 | 8.8598 | 16.2614 | 13.3533 | 12.484 | 19.9713 | 16.6902 | 22.4321 | 21.17 | 23.4533 | 31.0136
BLD6PRE |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_HEATCOIL | 3.9392 | 8.0209 | 5.7509 | 9.8372 | 4.4531 | 7.3636 | 5.7756 | 10.9247 | 8.8603 | 8.3127 | 13.5452 | 11.2176 | 15.2534 | 14.3305 | 15.9598 | 21.2146
BLD6PRE |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_HEATCOIL | 3.9393 | 8.0209 | 5.7507 | 9.8373 | 4.453 | 7.3639 | 5.7754 | 10.925 | 8.8603 | 8.3125 | 13.5453 | 11.2173 | 15.2537 | 14.331 | 15.96 | 21.2146
BLD6PRE |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_HEATCOIL | 3.9389 | 8.0393 | 5.7298 | 9.8349 | 4.4488 | 7.3368 | 5.7556 | 10.9181 | 8.8785 | 8.3203 | 13.5384 | 11.1876 | 15.266 | 14.3532 | 15.9687 | 21.2221
BLD6PRE |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_HEATCOIL | 3.939 | 8.0393 | 5.7295 | 9.8349 | 4.4487 | 7.3371 | 5.7554 | 10.9184 | 8.8785 | 8.3201 | 13.5385 | 11.1873 | 15.2662 | 14.3536 | 15.9689 | 21.2221
BLD6PRE |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_HEATCOIL | 6.5817 | 12.1036 | 9.1362 | 14.3618 | 7.3917 | 11.1481 | 9.1708 | 15.971 | 13.2093 | 12.4572 | 19.7212 | 16.599 | 21.9217 | 20.7508 | 23.0293 | 30.8771
BLD6PRE |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_HEATCOIL | 6.587 | 12.1038 | 9.1508 | 14.3794 | 7.3982 | 11.163 | 9.1842 | 15.9824 | 13.2133 | 12.4662 | 19.7357 | 16.6218 | 21.9338 | 20.7518 | 23.0455 | 30.8881
BLD6PRE |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_HEATCOIL | 6.5815 | 12.1036 | 9.1319 | 14.3565 | 7.3896 | 11.1522 | 9.1672 | 15.973 | 13.2093 | 12.4569 | 19.7186 | 16.5939 | 21.9235 | 20.7603 | 23.0292 | 30.8771
BLD6PRE |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_HEATCOIL | 2.6103 | 5.7798 | 4.5029 | 7.1238 | 3.4622 | 5.6981 | 4.404 | 7.9571 | 6.6575 | 6.1603 | 9.8253 | 8.3028 | 11.0717 | 10.511 | 11.6023 | 15.5315
BLD6PRE |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_HEATCOIL | 6.5869 | 12.1038 | 9.1466 | 14.3741 | 7.3961 | 11.1671 | 9.1806 | 15.9843 | 13.2133 | 12.4659 | 19.733 | 16.6167 | 21.9356 | 20.7614 | 23.0454 | 30.8881
BLD6PRE |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_HEATCOIL | 5.4565 | 10.0849 | 7.6264 | 11.9401 | 6.1564 | 9.2799 | 7.6604 | 13.3308 | 10.9816 | 10.3912 | 16.528 | 13.8901 | 18.3502 | 17.3495 | 19.3014 | 26.0005
BLD6PRE |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_HEATCOIL | 5.4565 | 10.0849 | 7.6263 | 11.94 | 6.1563 | 9.28 | 7.6603 | 13.3308 | 10.9816 | 10.3912 | 16.5279 | 13.89 | 18.3502 | 17.3497 | 19.3014 | 26.0005
BLD6PRE |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_HEATCOIL | 5.4505 | 10.0842 | 7.6109 | 11.9211 | 6.1494 | 9.264 | 7.6462 | 13.319 | 10.9773 | 10.382 | 16.5141 | 13.8677 | 18.339 | 17.3497 | 19.2862 | 25.9911
BLD6PRE |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_HEATCOIL | 5.4505 | 10.0842 | 7.6108 | 11.921 | 6.1494 | 9.2641 | 7.6461 | 13.319 | 10.9773 | 10.382 | 16.5141 | 13.8676 | 18.339 | 17.3499 | 19.2862 | 25.9911
BLD6PRE |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_HEATCOIL | 3.1618 | 7.2102 | 5.8932 | 8.5533 | 4.3775 | 7.2035 | 5.7338 | 9.3059 | 8.1437 | 7.5504 | 11.0265 | 9.6378 | 12.2233 | 11.753 | 12.7306 | 16.45
BLD6PRE |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_HEATCOIL | 2.612 | 5.7798 | 4.4991 | 7.1303 | 3.46 | 5.7046 | 4.4002 | 7.9658 | 6.6575 | 6.1543 | 9.8313 | 8.2955 | 11.0799 | 10.5182 | 11.6104 | 15.5315
BLD6PRE |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 3.8572 | 3.0475 | 4.8143 | 2.28 | 3.9052 | 2.9503 | 5.4325 | 4.5383 | 4.1839 | 6.7584 | 5.691 | 7.6369 | 7.2402 | 8.0132 | 10.7825
BLD6PRE |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 3.8572 | 3.0474 | 4.8144 | 2.28 | 3.9053 | 2.9502 | 5.4326 | 4.5383 | 4.1837 | 6.7585 | 5.6909 | 7.637 | 7.2403 | 8.0133 | 10.7825
BLD6PRE |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 3.8848 | 3.0524 | 4.8432 | 2.29 | 3.9079 | 2.9556 | 5.4499 | 4.5673 | 4.2074 | 6.7767 | 5.6969 | 7.669 | 7.2708 | 8.0452 | 10.8087
BLD6PRE |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 3.9964 | 3.1562 | 4.9602 | 2.3499 | 4.0235 | 3.0509 | 5.5682 | 4.6856 | 4.3211 | 6.8987 | 5.8182 | 7.7935 | 7.3962 | 8.171 | 10.9427
BLD6PRE |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_HEATCOIL | 6.2407 | 12.1215 | 8.828 | 14.744 | 6.9783 | 11.1473 | 8.8508 | 16.2418 | 13.3717 | 12.4999 | 19.9578 | 16.6734 | 22.4296 | 21.171 | 23.4491 | 31.017
BLD6PRE |  |  | HVAC Efficiency
BLD6PRE |  |  | Air Conditioning (COP)
BLD6PRE | COP |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38
BLD6PRE |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38
BLD6PRE |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38
BLD6PRE |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38
BLD6PRE |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38
BLD6PRE |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.38
BLD6PRE |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_COOLCOIL | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39 | 3.39
BLD6PRE |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_COOLCOIL | 3.38 | 3.38 | 3.38 | 3.38 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39 | 3.39 | 3.39 | 3.39 | 3.38 | 3.39 | 3.38 | 3.39
BLD6PRE |  |  | Heating Efficiency (%)
BLD6PRE |  |  | T CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6PRE |  |  | G CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6PRE |  |  | M CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6PRE | EffHeat |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
BLD6PRE |  |  | HVAC Control
BLD6PRE |  |  | Economizer | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
BLD6PRE | Fan |  | Fan Max Flow Rate (m3/s ) | 8.84 | 9.55 | 11.44 | 10.46 | 6.94 | 10.87 | 7.5 | 10.6 | 10.55 | 9.03 | 12.76 | 12.84 | 14.4 | 15.36 | 15.42 | 20.04
BLD6PRE |  |  | T CORRIDOR UNIT HEATERFAN | 0 | 0.07 | 0.02 | 0.11 | 0 | 0.06 | 0.02 | 0.14 | 0.11 | 0.07 | 0.21 | 0.19 | 0.24 | 0.26 | 0.27 | 0.41
BLD6PRE |  |  | G CORRIDOR UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | M CORRIDOR UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_FAN | 0.27 | 0.28 | 0.31 | 0.28 | 0.23 | 0.29 | 0.22 | 0.28 | 0.29 | 0.23 | 0.35 | 0.35 | 0.39 | 0.42 | 0.42 | 0.55
BLD6PRE |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_FAN | 0.68 | 0.69 | 0.81 | 0.69 | 0.47 | 0.78 | 0.41 | 0.61 | 0.6 | 0.47 | 0.7 | 0.71 | 0.8 | 0.85 | 0.85 | 1.09
BLD6PRE |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_FAN | 0.47 | 0.5 | 0.65 | 0.54 | 0.45 | 0.63 | 0.53 | 0.57 | 0.58 | 0.56 | 0.7 | 0.71 | 0.8 | 0.85 | 0.85 | 1.09
BLD6PRE |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_FAN | 0.48 | 0.48 | 0.59 | 0.54 | 0.31 | 0.53 | 0.31 | 0.57 | 0.57 | 0.44 | 0.71 | 0.71 | 0.8 | 0.85 | 0.85 | 1.09
BLD6PRE |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_FAN | 0.36 | 0.36 | 0.43 | 0.36 | 0.21 | 0.41 | 0.17 | 0.34 | 0.34 | 0.25 | 0.42 | 0.42 | 0.48 | 0.5 | 0.51 | 0.66
BLD6PRE |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_FAN | 0.35 | 0.36 | 0.43 | 0.35 | 0.2 | 0.41 | 0.17 | 0.34 | 0.34 | 0.25 | 0.42 | 0.42 | 0.48 | 0.5 | 0.51 | 0.66
BLD6PRE |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_FAN | 0.29 | 0.34 | 0.45 | 0.37 | 0.35 | 0.45 | 0.47 | 0.38 | 0.34 | 0.46 | 0.42 | 0.42 | 0.48 | 0.51 | 0.51 | 0.66
BLD6PRE |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_FAN | 0.29 | 0.34 | 0.45 | 0.37 | 0.35 | 0.45 | 0.47 | 0.38 | 0.34 | 0.46 | 0.42 | 0.42 | 0.48 | 0.51 | 0.51 | 0.66
BLD6PRE |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_FAN | 0.67 | 0.73 | 0.89 | 0.73 | 0.54 | 0.85 | 0.54 | 0.65 | 0.63 | 0.59 | 0.79 | 0.79 | 0.88 | 0.94 | 0.95 | 1.23
BLD6PRE |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_FAN | 0.54 | 0.57 | 0.68 | 0.59 | 0.36 | 0.64 | 0.36 | 0.63 | 0.63 | 0.49 | 0.79 | 0.79 | 0.88 | 0.94 | 0.95 | 1.23
BLD6PRE |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_FAN | 0.41 | 0.48 | 0.61 | 0.59 | 0.34 | 0.57 | 0.36 | 0.63 | 0.63 | 0.49 | 0.79 | 0.79 | 0.88 | 0.94 | 0.95 | 1.23
BLD6PRE |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_FAN | 0.29 | 0.3 | 0.32 | 0.29 | 0.19 | 0.29 | 0.15 | 0.28 | 0.29 | 0.22 | 0.35 | 0.35 | 0.39 | 0.42 | 0.42 | 0.55
BLD6PRE |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_FAN | 0.41 | 0.48 | 0.56 | 0.59 | 0.29 | 0.52 | 0.36 | 0.63 | 0.63 | 0.49 | 0.79 | 0.79 | 0.88 | 0.94 | 0.95 | 1.23
BLD6PRE |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_FAN | 0.36 | 0.39 | 0.47 | 0.48 | 0.24 | 0.43 | 0.29 | 0.51 | 0.52 | 0.4 | 0.64 | 0.65 | 0.72 | 0.77 | 0.77 | 1.01
BLD6PRE |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_FAN | 0.36 | 0.39 | 0.47 | 0.48 | 0.24 | 0.43 | 0.29 | 0.51 | 0.52 | 0.4 | 0.64 | 0.65 | 0.72 | 0.77 | 0.77 | 1.01
BLD6PRE |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_FAN | 0.35 | 0.4 | 0.51 | 0.48 | 0.29 | 0.48 | 0.31 | 0.51 | 0.52 | 0.4 | 0.64 | 0.65 | 0.72 | 0.77 | 0.77 | 1.01
BLD6PRE |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_FAN | 0.35 | 0.4 | 0.51 | 0.48 | 0.29 | 0.48 | 0.31 | 0.51 | 0.52 | 0.4 | 0.64 | 0.65 | 0.72 | 0.77 | 0.77 | 1.01
BLD6PRE |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_FAN | 0.37 | 0.37 | 0.42 | 0.39 | 0.33 | 0.39 | 0.31 | 0.37 | 0.4 | 0.34 | 0.45 | 0.47 | 0.5 | 0.54 | 0.53 | 0.66
BLD6PRE |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_FAN | 0.2 | 0.2 | 0.22 | 0.26 | 0.12 | 0.22 | 0.15 | 0.28 | 0.29 | 0.22 | 0.35 | 0.35 | 0.39 | 0.42 | 0.42 | 0.55
BLD6PRE |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_FAN | 0.15 | 0.15 | 0.15 | 0.15 | 0.07 | 0.13 | 0.09 | 0.17 | 0.17 | 0.13 | 0.21 | 0.21 | 0.24 | 0.26 | 0.26 | 0.34
BLD6PRE |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_FAN | 0.15 | 0.14 | 0.14 | 0.15 | 0.07 | 0.13 | 0.09 | 0.17 | 0.17 | 0.13 | 0.21 | 0.21 | 0.24 | 0.26 | 0.26 | 0.34
BLD6PRE |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_FAN | 0.12 | 0.14 | 0.16 | 0.16 | 0.14 | 0.15 | 0.14 | 0.17 | 0.18 | 0.15 | 0.21 | 0.21 | 0.24 | 0.26 | 0.26 | 0.34
BLD6PRE |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_FAN | 0.12 | 0.14 | 0.16 | 0.16 | 0.14 | 0.15 | 0.14 | 0.17 | 0.18 | 0.15 | 0.21 | 0.22 | 0.25 | 0.26 | 0.26 | 0.34
BLD6PRE |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_FAN | 0.8 | 0.85 | 1.03 | 0.87 | 0.72 | 1 | 0.84 | 0.8 | 0.76 | 0.84 | 0.7 | 0.71 | 0.8 | 0.85 | 0.85 | 1.09
BLD6PRE |  | Utility Costs
BLD6PRE |  |  | Electric Utility Rates
BLD6PRE |  |  | Average Annual Rate ($/kWh) | 0.080264 | 0.12111 | 0.10123 | 0.10354 | 0.12843 | 0.096977 | 0.14807 | 0.07353 | 0.037604 | 0.072332 | 0.052755 | 0.037664 | 0.058352 | 0.072865 | 0.056277 | 0.092874
BLD6PRE |  |  | Total Cost ($/m2) | 10.39 | 13.66 | 12.73 | 10.01 | 10.38 | 10.85 | 11.15 | 6.72 | 3.42 | 5.64 | 4.55 | 3.14 | 5.09 | 5.99 | 4.7 | 8.32
BLD6PRE |  |  | Gas Utility Rates
BLD6PRE |  |  | Average Annual Rate ($/MJ) | 0.011437 | 0.0080932 | 0.0082806 | 0.009783 | 0.0085585 | 0.0077469 | 0.0085405 | 0.0097289 | 0.006938 | 0.0084001 | 0.0084187 | 0.0069642 | 0.0078771 | 0.0082087 | 0.0078742 | 0.0041394
BLD6PRE |  |  | Total Cost ($/m2) | 0.71 | 1.65 | 1.29 | 3.43 | 1.39 | 1.86 | 2.84 | 5.25 | 2.77 | 4.56 | 5.61 | 3.71 | 6.41 | 5.8 | 7.88 | 6.24
BLD6PRE |  |  | Total Utility Costs
BLD6PRE |  |  | Cost Intensity ($/m2) | 11.1 | 15.31 | 14.02 | 13.44 | 11.77 | 12.71 | 13.99 | 11.97 | 6.19 | 10.2 | 10.16 | 6.85 | 11.5 | 11.8 | 12.58 | 14.56
BLD6PRE |  | Energy - End Uses
BLD6PRE |  |  | Electricity (kWh)
BLD6PRE |  |  | Heating | 0 | 177.7778 | 11.1111 | 558.3333 | 0 | 55.5556 | 8.3333 | 1272.2222 | 427.7778 | 155.5556 | 2236.1111 | 1233.3333 | 4416.6667 | 2519.4444 | 5925 | 14680.5556
BLD6PRE |  |  | Cooling | 158791.6667 | 111208.3333 | 145866.6667 | 63747.2222 | 26930.5556 | 105061.1111 | 8169.4444 | 45300 | 44055.5556 | 9680.5556 | 27461.1111 | 21050 | 24194.4444 | 12488.8889 | 7794.4444 | 3847.2222
BLD6PRE |  |  | Interior Lighting | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889
BLD6PRE |  |  | Exterior Lighting | 28130.5556 | 28122.2222 | 28116.6667 | 28111.1111 | 28088.8889 | 28083.3333 | 28097.2222 | 28080.5556 | 28091.6667 | 28036.1111 | 28086.1111 | 28069.4444 | 28066.6667 | 28061.1111 | 28044.4444 | 27872.2222
BLD6PRE |  |  | Interior Equipment | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500
BLD6PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Fans | 30672.2222 | 25980.5556 | 32044.4444 | 22377.7778 | 10230.5556 | 29361.1111 | 11641.6667 | 23786.1111 | 24297.2222 | 18616.6667 | 24655.5556 | 23041.6667 | 28527.7778 | 26613.8889 | 31897.2222 | 46272.2222
BLD6PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Total End Uses | 405733.3333 | 353625 | 394175 | 302933.3333 | 253391.6667 | 350700 | 236058.3333 | 286580.5556 | 285008.3333 | 244625 | 270575 | 261536.1111 | 273344.4444 | 257825 | 261800 | 280811.1111
BLD6PRE |  |  | Gas (MJ)
BLD6PRE |  |  | Heating | 27580 | 429120 | 302650 | 847200 | 266300 | 536350 | 763460 | 1406800 | 974770 | 1399240 | 1774800 | 1357310 | 2213040 | 1873240 | 2759070 | 4297670
BLD6PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Water Systems | 166570 | 209980 | 185050 | 251800 | 243660 | 215100 | 279450 | 284660 | 278430 | 301760 | 313510 | 312000 | 338430 | 342960 | 379550 | 429320
BLD6PRE |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Total End Uses | 194150 | 639100 | 487700 | 1098990 | 509970 | 751450 | 1042910 | 1691470 | 1253200 | 1700990 | 2088300 | 1669310 | 2551480 | 2216200 | 3138620 | 4726980
BLD6PRE |  |  | Total Building (MJ) | 1654790 | 1912150 | 1906730 | 2189550 | 1422170 | 2013970 | 1892710 | 2723150 | 2279240 | 2581640 | 3062380 | 2610840 | 3535520 | 3144370 | 4081100 | 5737910
BLD6PRE |  | Energy - End Use Intensities
BLD6PRE |  |  | Electricity (MJ/m2)
BLD6PRE |  |  | Heating (elec) | 0 | 0.20417 | 0.012761 | 0.64123 | 0 | 0.063804 | 0.0095706 | 1.4611 | 0.49129 | 0.17865 | 2.5681 | 1.4165 | 5.0724 | 2.8935 | 6.8047 | 16.8603
BLD6PRE |  |  | Cooling (elec) | 182.3683 | 127.7201 | 167.5243 | 73.2121 | 30.9291 | 120.6601 | 9.3824 | 52.0259 | 50.5967 | 11.1179 | 31.5384 | 24.1754 | 27.7867 | 14.3432 | 8.9517 | 4.4184
BLD6PRE |  |  | Interior Lighting (elec) | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877
BLD6PRE |  |  | Exterior Lighting (elec) | 32.3073 | 32.2977 | 32.2913 | 32.2849 | 32.2594 | 32.253 | 32.269 | 32.2498 | 32.2626 | 32.1988 | 32.2562 | 32.2371 | 32.2339 | 32.2275 | 32.2084 | 32.0106
BLD6PRE |  |  | Interior Equipment (elec) | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852
BLD6PRE |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Fans (elec) | 35.2263 | 29.838 | 36.8023 | 25.7003 | 11.7495 | 33.7205 | 13.3702 | 27.3178 | 27.9048 | 21.3808 | 28.3163 | 26.4628 | 32.7635 | 30.5654 | 36.6332 | 53.1425
BLD6PRE |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Total End Uses | 465.9748 | 406.1297 | 452.7004 | 347.9115 | 291.0141 | 402.7704 | 271.1072 | 329.1308 | 327.3251 | 280.9458 | 310.7488 | 300.3678 | 313.9294 | 296.1057 | 300.6709 | 322.5047
BLD6PRE |  |  | Gas (MJ/m2)
BLD6PRE |  |  | Heating (gas) | 8.7986 | 136.8983 | 96.5517 | 270.2746 | 84.9553 | 171.1069 | 243.5598 | 448.7987 | 310.9721 | 446.3869 | 566.1985 | 433.0104 | 706.0062 | 597.6029 | 880.2012 | 1371.0469
BLD6PRE |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Water Systems (gas) | 53.1393 | 66.988 | 59.0348 | 80.3295 | 77.7327 | 68.6214 | 89.1504 | 90.8125 | 88.825 | 96.2678 | 100.0163 | 99.5345 | 107.9663 | 109.4114 | 121.0844 | 136.9621
BLD6PRE |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Total End Uses | 61.9379 | 203.8863 | 155.5865 | 350.6009 | 162.6911 | 239.7283 | 332.7102 | 539.6144 | 399.7971 | 542.6515 | 666.2115 | 532.5449 | 813.9757 | 707.0143 | 1001.2857 | 1508.0058
BLD6PRE |  |  | Total Building (MJ/m2) | 527.9127 | 610.016 | 608.2869 | 698.5124 | 453.7021 | 642.4987 | 603.8142 | 868.742 | 727.1254 | 823.5973 | 976.9635 | 832.9128 | 1127.9051 | 1003.12 | 1301.9566 | 1830.5137
BLD6PRE |  | Peak Energy Demand
BLD6PRE |  |  | Electricity Peak Demand (kW)
BLD6PRE |  |  | Jan | 67.3129 | 55.0936 | 52.777 | 50.9603 | 48.0811 | 46.7236 | 44.744 | 53.2493 | 46.3458 | 46.5474 | 53.9921 | 52.4859 | 56.4682 | 55.6294 | 57.5826 | 66.4185
BLD6PRE |  |  | Feb | 71.1021 | 60.3033 | 57.9186 | 48.8844 | 45.5072 | 44.9555 | 44.8548 | 47.7522 | 45.9054 | 45.7939 | 49.8279 | 51.2581 | 54.2133 | 53.0209 | 57.3446 | 65.1749
BLD6PRE |  |  | Mar | 78.5272 | 76.7121 | 79.8253 | 53.7667 | 47.8066 | 50.2688 | 43.3217 | 44.5663 | 44.588 | 45.3015 | 47.4524 | 48.2833 | 50.0246 | 49.1202 | 51.2687 | 54.6103
BLD6PRE |  |  | Apr | 84.3323 | 83.1133 | 84.2756 | 71.0125 | 58.9781 | 78.3153 | 44.5701 | 51.8911 | 60.1735 | 44.3981 | 44.4226 | 48.4917 | 43.8795 | 43.5322 | 44.7002 | 49.7687
BLD6PRE |  |  | May | 88.7294 | 100.7171 | 115.1591 | 84.5926 | 55.721 | 94.9026 | 43.512 | 66.624 | 73.5763 | 50.9305 | 63.2251 | 60.37 | 82.1914 | 46.6208 | 44.0096 | 40.589
BLD6PRE |  |  | Jun | 99.1436 | 102.6517 | 137.531 | 95.5061 | 56.1515 | 120.8525 | 51.1686 | 103.5831 | 83.9071 | 62.6806 | 75.2253 | 69.3649 | 84.2298 | 72.0512 | 62.3734 | 57.3594
BLD6PRE |  |  | Jul | 96.5674 | 107.6208 | 136.8664 | 110.9204 | 63.1442 | 118.7403 | 73.8884 | 101.5126 | 90.1827 | 69.177 | 90.0015 | 76.8496 | 85.1329 | 76.4167 | 76.2374 | 62.9542
BLD6PRE |  |  | Aug | 98.565 | 106.4549 | 137.1135 | 95.0261 | 68.0132 | 116.8073 | 49.1605 | 104.6321 | 88.4756 | 66.8154 | 87.0058 | 74.5365 | 83.4925 | 70.231 | 70.9964 | 53.919
BLD6PRE |  |  | Sep | 90.8424 | 95.7764 | 121.27 | 80.6717 | 68.5292 | 107.8813 | 76.2725 | 79.9015 | 73.3682 | 86.731 | 64.7105 | 68.0422 | 59.3822 | 60.0239 | 47.2096 | 44.1014
BLD6PRE |  |  | Oct | 88.8115 | 83.1994 | 85.9496 | 72.298 | 55.6904 | 80.1285 | 50.0706 | 60.7765 | 63.1828 | 45.6477 | 50.0763 | 53.8237 | 52.6636 | 45.758 | 46.117 | 52.2496
BLD6PRE |  |  | Nov | 75.97 | 64.4059 | 66.6892 | 46.5452 | 45.3634 | 44.876 | 43.2592 | 49.2131 | 46.1577 | 46.4603 | 46.2745 | 47.7076 | 49.5971 | 47.403 | 53.126 | 58.3747
BLD6PRE |  |  | Dec | 67.2099 | 57.6819 | 48.5901 | 47.5905 | 45.2013 | 44.8392 | 44.1572 | 48.8993 | 48.481 | 47.1868 | 55.0551 | 52.9444 | 56.3165 | 55.9778 | 56.9056 | 64.4567
BLD6PRE |  |  | Time of Peak Electrical Demand
BLD6PRE |  |  | Jan | 23-JAN-18:10 | 20-JAN-18:10 | 28-JAN-18:10 | 13-JAN-18:00 | 25-JAN-17:19 | 10-JAN-18:00 | 29-JAN-18:00 | 17-JAN-19:00 | 03-JAN-18:00 | 31-JAN-18:00 | 07-JAN-18:00 | 05-JAN-20:00 | 04-JAN-18:00 | 16-JAN-18:00 | 08-JAN-18:00 | 12-JAN-18:10
BLD6PRE |  |  | Feb | 24-FEB-18:19 | 23-FEB-16:10 | 28-FEB-18:19 | 13-FEB-18:00 | 12-FEB-17:30 | 07-FEB-17:10 | 15-FEB-18:10 | 04-FEB-18:00 | 05-FEB-18:00 | 28-FEB-18:00 | 08-FEB-18:00 | 15-FEB-18:00 | 03-FEB-18:00 | 25-FEB-18:00 | 01-FEB-18:00 | 04-FEB-18:00
BLD6PRE |  |  | Mar | 13-MAR-16:19 | 26-MAR-16:10 | 17-MAR-16:19 | 28-MAR-17:10 | 31-MAR-16:10 | 31-MAR-16:10 | 06-MAR-18:00 | 21-MAR-18:00 | 27-MAR-18:00 | 01-MAR-18:00 | 03-MAR-18:00 | 06-MAR-20:00 | 05-MAR-20:00 | 02-MAR-18:00 | 02-MAR-20:00 | 11-MAR-18:00
BLD6PRE |  |  | Apr | 01-APR-16:10 | 29-APR-16:10 | 01-APR-17:10 | 15-APR-16:10 | 11-APR-16:10 | 21-APR-16:10 | 13-APR-16:10 | 05-APR-17:10 | 21-APR-17:10 | 11-APR-18:00 | 02-APR-18:19 | 26-APR-18:49 | 03-APR-18:00 | 17-APR-19:00 | 22-APR-18:00 | 01-APR-19:00
BLD6PRE |  |  | May | 15-MAY-17:10 | 26-MAY-17:19 | 28-MAY-17:10 | 14-MAY-17:30 | 29-MAY-17:10 | 31-MAY-16:19 | 25-MAY-17:10 | 15-MAY-17:10 | 31-MAY-17:10 | 15-MAY-17:10 | 30-MAY-17:10 | 23-MAY-17:10 | 27-MAY-17:10 | 16-MAY-17:10 | 31-MAY-17:10 | 24-MAY-17:30
BLD6PRE |  |  | Jun | 27-JUN-17:10 | 13-JUN-17:10 | 28-JUN-17:19 | 19-JUN-17:10 | 30-JUN-17:10 | 27-JUN-16:19 | 16-JUN-16:10 | 30-JUN-17:10 | 20-JUN-17:10 | 18-JUN-16:10 | 20-JUN-15:09 | 27-JUN-16:10 | 29-JUN-17:19 | 25-JUN-17:00 | 14-JUN-17:19 | 20-JUN-17:00
BLD6PRE |  |  | Jul | 12-JUL-17:10 | 30-JUL-16:10 | 19-JUL-17:19 | 03-JUL-16:19 | 10-JUL-17:10 | 24-JUL-16:19 | 02-JUL-17:10 | 25-JUL-16:10 | 31-JUL-17:10 | 24-JUL-17:00 | 13-JUL-17:10 | 17-JUL-16:10 | 15-JUL-17:10 | 21-JUL-17:10 | 06-JUL-17:19 | 29-JUL-17:49
BLD6PRE |  |  | Aug | 21-AUG-16:19 | 27-AUG-17:10 | 01-AUG-17:10 | 14-AUG-17:10 | 08-AUG-16:19 | 04-AUG-16:19 | 26-AUG-17:10 | 17-AUG-16:19 | 01-AUG-16:10 | 06-AUG-17:10 | 04-AUG-17:10 | 29-AUG-17:10 | 25-AUG-17:10 | 09-AUG-17:10 | 13-AUG-17:10 | 15-AUG-17:10
BLD6PRE |  |  | Sep | 09-SEP-16:10 | 15-SEP-16:19 | 09-SEP-16:10 | 05-SEP-16:19 | 25-SEP-15:09 | 01-SEP-15:09 | 28-SEP-16:10 | 09-SEP-16:10 | 02-SEP-17:10 | 02-SEP-16:10 | 27-SEP-16:10 | 02-SEP-16:10 | 14-SEP-16:10 | 01-SEP-17:10 | 08-SEP-18:40 | 29-SEP-18:00
BLD6PRE |  |  | Oct | 06-OCT-16:19 | 06-OCT-16:10 | 13-OCT-16:19 | 01-OCT-16:10 | 05-OCT-17:40 | 03-OCT-16:10 | 13-OCT-16:10 | 12-OCT-16:10 | 01-OCT-16:10 | 17-OCT-17:19 | 31-OCT-17:10 | 05-OCT-16:10 | 08-OCT-17:40 | 06-OCT-17:00 | 31-OCT-17:00 | 30-OCT-17:00
BLD6PRE |  |  | Nov | 01-NOV-17:40 | 01-NOV-16:10 | 13-NOV-16:10 | 19-NOV-17:30 | 09-NOV-17:10 | 10-NOV-17:10 | 22-NOV-18:49 | 05-NOV-17:10 | 19-NOV-18:00 | 29-NOV-18:00 | 02-NOV-17:19 | 18-NOV-18:00 | 27-NOV-18:10 | 29-NOV-18:00 | 24-NOV-18:00 | 22-NOV-18:00
BLD6PRE |  |  | Dec | 17-DEC-17:30 | 02-DEC-18:19 | 11-DEC-17:19 | 21-DEC-18:00 | 19-DEC-12:00 | 30-DEC-18:00 | 28-DEC-18:00 | 20-DEC-18:00 | 28-DEC-18:00 | 13-DEC-18:00 | 31-DEC-18:00 | 11-DEC-20:00 | 31-DEC-18:00 | 11-DEC-18:00 | 31-DEC-18:00 | 29-DEC-18:10
BLD6PRE |  | Source Energy
BLD6PRE |  |  | Total Source Energy (GJ) | 5056.96 | 5321.62 | 5020.96 | 4868.73 | 3380.16 | 5336.62 | 3769 | 5536.39 | 4772.88 | 3391.58 | 5734.49 | 4946.87 | 6168.35 | 5646.4 | 6666.66 | 8772.88
BLD6PRE |  |  | Total Source Energy (MJ/m2) | 1613.27 | 1697.71 | 1601.79 | 1553.23 | 1078.34 | 1702.49 | 1202.39 | 1766.22 | 1522.65 | 1081.98 | 1829.42 | 1578.15 | 1967.83 | 1801.32 | 2126.8 | 2798.73
BLD6PRE |  | Water Consumption (m3)
BLD6PRE |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Water Systems | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51
BLD6PRE |  |  | Total Building | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51
BLD6PRE |  | Emissions
BLD6PRE |  |  | Carbon Equivalent (kg) | 114773.3147 | 129480.2499 | 127786.1902 | 113132.1726 | 38808.8126 | 131832.9422 | 46393.4709 | 107836.7089 | 139024.4167 | 48490.5934 | 181914.8626 | 136938.6828 | 139573.6789 | 134182.6616 | 146209.6898 | 164257.2039
BLD6PRE |  |  | CO2 (kg) | 267772.1685 | 329281.3747 | 305241.617 | 269043.7593 | 105630.2573 | 319303.5532 | 127988.163 | 261551.7091 | 336575.2298 | 130945.8603 | 441640.8451 | 335910.485 | 348632.9407 | 334604.1587 | 370112.6865 | 444214.4118
BLD6PRE |  |  | NOX (kg) | 463.5883 | 419.2737 | 496.0304 | 460.9414 | 91.7798 | 494.9742 | 112.3596 | 426.7558 | 535.2535 | 148.4608 | 704.844 | 515.732 | 514.2997 | 493.8207 | 525.4468 | 471.5655
BLD6PRE |  |  | SO2 (kg) | 1736.7519 | 1686.9631 | 1585.1851 | 1063.5881 | 737.4736 | 1929.3293 | 687.1778 | 1046.5823 | 1244.9145 | 189.5314 | 1824.0213 | 1142.5174 | 645.8183 | 689.0146 | 618.7278 | 1430.7109
BLD6PRE |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PRE |  |  | Hg (kg) | 0.0079 | 0.0048 | 0.0044 | 0.004 | 0.0004 | 0.0037 | 0.0004 | 0.0044 | 0.005 | 0.0009 | 0.0057 | 0.0046 | 0.005 | 0.005 | 0.0049 | 0.0054
BLD6PRE |  |  | Water for Electricity (m3) | 214.9403 | 575.3895 | 11708.7 | 1891.39 | 4448.98 | 9621.09 | 4144.64 | 65.0643 | 1294.17 | 2499.28 | 419.7815 | 1187.58 | 424.0762 | 16331.6 | 406.1649 | 286.8997
BLD6PST |  | Location Summary
BLD6PST |  |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD6PST |  | Program
BLD6PST |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD6PST |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD6PST |  |  | Weighting Factor
BLD6PST |  | Fabric
BLD6PST |  |  | Exterior walls
BLD6PST | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD6PST | RvalWall |  | R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
BLD6PST |  |  | Roof
BLD6PST | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD6PST | RvalRoof |  | R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
BLD6PST |  |  | Window
BLD6PST | Uwindow |  | U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
BLD6PST | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
BLD6PST |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
BLD6PST |  |  | Skylights/TDD
BLD6PST |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD6PST |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD6PST |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD6PST |  |  | Foundation
BLD6PST |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD6PST |  |  | Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
BLD6PST |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD6PST |  | HVAC
BLD6PST |  |  | HVAC Sizing
BLD6PST | HVAC |  | Air Conditioning (kW) | 252.209 | 186.5944 | 224.877 | 202.4762 | 146.0699 | 179.3843 | 110.8242 | 208.9728 | 169.4711 | 142.5729 | 277.4041 | 228.9291 | 306.8673 | 243.3185 | 325.3708 | 302.8177
BLD6PST |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 8.6952 | 5.019 | 6.6411 | 5.3854 | 4.6109 | 4.7158 | 2.5196 | 5.6189 | 4.8559 | 3.7203 | 7.5928 | 6.5179 | 8.4211 | 6.8181 | 9.025 | 8.0932
BLD6PST |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_COOLCOIL | 21.277 | 12.2301 | 16.1977 | 11.0464 | 9.6562 | 12.0813 | 5.6886 | 11.1398 | 8.6357 | 7.0333 | 15.1689 | 11.6988 | 16.6652 | 12.654 | 17.8032 | 15.7747
BLD6PST |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_COOLCOIL | 14.5391 | 9.3482 | 14.2457 | 10.9057 | 9.0367 | 10.7551 | 6.9883 | 11.1378 | 9.3887 | 7.6094 | 15.1635 | 12.5703 | 16.6747 | 13.5251 | 17.8098 | 16.2098
BLD6PST |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_COOLCOIL | 14.8955 | 9.3351 | 12.871 | 10.9103 | 6.7328 | 9.5249 | 5.1046 | 11.1449 | 9.5679 | 7.5851 | 15.1724 | 13.0087 | 16.6724 | 13.8693 | 17.8095 | 16.2345
BLD6PST |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_COOLCOIL | 10.63 | 7.1044 | 9.7575 | 6.5898 | 4.8315 | 7.5448 | 2.9721 | 6.375 | 5.1111 | 4.0531 | 8.8691 | 6.9454 | 9.7674 | 7.6541 | 10.4561 | 9.1192
BLD6PST |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_COOLCOIL | 10.5246 | 7.0517 | 9.6889 | 6.543 | 4.6989 | 7.5026 | 2.8902 | 6.3751 | 5.119 | 4.0589 | 8.8692 | 6.9552 | 9.7675 | 7.6579 | 10.4563 | 9.1192
BLD6PST |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_COOLCOIL | 8.7205 | 6.5603 | 10.0572 | 6.4318 | 7.2803 | 8.146 | 6.122 | 6.3703 | 5.2757 | 6.218 | 8.8635 | 7.0932 | 9.7735 | 7.6987 | 10.4606 | 9.7286
BLD6PST |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_COOLCOIL | 8.7408 | 6.5702 | 10.0716 | 6.3958 | 7.2958 | 8.1513 | 6.132 | 6.3704 | 5.2835 | 6.2323 | 8.8636 | 7.1032 | 9.7737 | 7.7036 | 10.4608 | 9.7263
BLD6PST |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_COOLCOIL | 17.9608 | 12.987 | 14.7585 | 12.7968 | 10.4353 | 11.397 | 6.6234 | 13.541 | 9.9754 | 8.2252 | 17.8763 | 13.7098 | 19.8588 | 14.7636 | 21.1193 | 18.8142
BLD6PST |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_COOLCOIL | 15.0096 | 10.6814 | 12.0437 | 12.8134 | 7.6063 | 9.0896 | 6.2489 | 13.5539 | 10.387 | 8.6127 | 17.8914 | 14.3889 | 19.8728 | 15.182 | 21.1353 | 18.8523
BLD6PST |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_COOLCOIL | 10.0457 | 10.6795 | 10.8897 | 12.794 | 7.1085 | 9.0279 | 6.2425 | 13.5418 | 10.8807 | 8.68 | 17.8743 | 15.1174 | 19.8599 | 15.9111 | 21.1192 | 19.2797
BLD6PST |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_COOLCOIL | 9.7535 | 5.1936 | 6.688 | 5.3687 | 4.0257 | 4.6315 | 2.573 | 5.611 | 4.8412 | 3.8181 | 7.5825 | 6.6089 | 8.4049 | 6.8127 | 9.0088 | 8.1488
BLD6PST |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_COOLCOIL | 10.4224 | 10.6814 | 10.2057 | 12.8106 | 6.9608 | 9.1167 | 6.5074 | 13.5546 | 10.9027 | 8.9143 | 17.8894 | 15.1581 | 19.8739 | 16.038 | 21.1353 | 19.9332
BLD6PST |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_COOLCOIL | 9.106 | 8.6821 | 8.5233 | 10.4965 | 5.7248 | 7.2878 | 5.3889 | 11.1772 | 8.9309 | 7.3552 | 14.7427 | 12.5493 | 16.4248 | 13.0751 | 17.4602 | 15.4392
BLD6PST |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_COOLCOIL | 9.0378 | 8.6821 | 8.4795 | 10.4965 | 5.7277 | 7.2944 | 5.3985 | 11.1772 | 8.9373 | 7.3596 | 14.7427 | 12.5571 | 16.4248 | 13.0784 | 17.4602 | 16.5859
BLD6PST |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_COOLCOIL | 8.0526 | 8.6805 | 8.8558 | 10.4805 | 6.299 | 7.385 | 5.172 | 11.1655 | 8.9576 | 7.1918 | 14.7291 | 12.4007 | 16.4125 | 13.0025 | 17.4461 | 16.1188
BLD6PST |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_COOLCOIL | 8.0418 | 8.6805 | 8.8556 | 10.4804 | 6.3022 | 7.398 | 5.1717 | 11.1655 | 8.9621 | 7.1911 | 14.729 | 12.4389 | 16.4126 | 13.0049 | 17.4461 | 16.1141
BLD6PST |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_COOLCOIL | 9.6842 | 7.7502 | 8.107 | 7.1969 | 5.9954 | 6.2907 | 4.0713 | 7.6555 | 5.9019 | 4.8389 | 9.6734 | 7.2768 | 10.2874 | 7.825 | 10.2535 | 9.6101
BLD6PST |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_COOLCOIL | 6.7693 | 4.4659 | 4.7399 | 5.372 | 2.921 | 4.8393 | 2.7554 | 5.6141 | 5.5993 | 4.1934 | 7.5867 | 7.3297 | 8.4095 | 7.6486 | 9.0135 | 8.5014
BLD6PST |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_COOLCOIL | 4.5074 | 2.8001 | 3.2558 | 3.1598 | 1.6699 | 3.011 | 1.5565 | 3.3258 | 3.0268 | 2.2919 | 4.552 | 4.0119 | 5.0684 | 4.256 | 5.4515 | 7.2291
BLD6PST |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_COOLCOIL | 4.4571 | 2.7756 | 3.2255 | 3.1599 | 1.6699 | 3.0111 | 1.5662 | 3.3258 | 3.0301 | 2.2946 | 4.5521 | 4.0166 | 5.0685 | 4.2585 | 5.4515 | 7.2291
BLD6PST |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_COOLCOIL | 3.6822 | 2.5903 | 3.4645 | 3.1791 | 2.9661 | 3.0143 | 1.5411 | 3.3367 | 3.1671 | 2.397 | 4.5655 | 4.1442 | 5.0879 | 4.2865 | 5.4711 | 5.5888
BLD6PST |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_COOLCOIL | 3.8124 | 2.7174 | 3.6014 | 3.3058 | 3.0606 | 3.1472 | 1.629 | 3.4592 | 3.2853 | 2.4813 | 4.6942 | 4.2558 | 5.2179 | 4.3808 | 5.6045 | 5.6578
BLD6PST |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_COOLCOIL | 23.8435 | 15.3279 | 19.6521 | 14.3574 | 13.4537 | 15.021 | 9.9609 | 13.2358 | 9.4481 | 10.2175 | 15.16 | 11.0723 | 16.6674 | 12.2143 | 16.5132 | 15.7099
BLD6PST | HEAT |  | Heating (kW) | 132.396 | 192.1749 | 152.1751 | 222.8413 | 122.7435 | 177.7299 | 137.6554 | 244.542 | 202.1118 | 192.4166 | 321.5583 | 263.2391 | 355.212 | 337.5726 | 370.9174 | 496.7395
BLD6PST |  |  | T CORRIDOR UNIT HEATER COIL | 0 | 1.3825 | 0 | 2.4104 | 0 | 0.75397 | 0.13806 | 3.0706 | 1.9301 | 1.5694 | 5.261 | 3.7321 | 6.2799 | 5.9659 | 6.7172 | 10.3569
BLD6PST |  |  | G CORRIDOR UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | M CORRIDOR UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 3.5669 | 5.3206 | 4.5516 | 6.186 | 3.434 | 5.2902 | 3.8123 | 6.7902 | 5.7566 | 5.3696 | 8.9377 | 7.4057 | 9.8792 | 9.4096 | 10.3479 | 13.9236
BLD6PST |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_HEATCOIL | 8.4598 | 10.9739 | 8.9524 | 12.4947 | 6.8926 | 10.2072 | 7.4547 | 13.4906 | 11.2072 | 10.5917 | 17.8605 | 14.6029 | 19.6002 | 18.5737 | 20.4798 | 27.3169
BLD6PST |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_HEATCOIL | 8.4819 | 10.986 | 8.9225 | 12.4919 | 6.8844 | 10.1965 | 7.4423 | 13.4887 | 11.2123 | 10.5885 | 17.8556 | 14.5732 | 19.6087 | 18.589 | 20.4856 | 27.3142
BLD6PST |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_HEATCOIL | 8.4672 | 10.9739 | 8.9423 | 12.496 | 6.8874 | 10.2168 | 7.4517 | 13.4953 | 11.2072 | 10.5879 | 17.8637 | 14.5944 | 19.6067 | 18.5829 | 20.4853 | 27.3169
BLD6PST |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_HEATCOIL | 5.4213 | 7.2812 | 5.8204 | 8.3646 | 4.3944 | 6.7288 | 4.8382 | 9.1225 | 7.4558 | 7.0667 | 12.1811 | 9.8546 | 13.429 | 12.6631 | 14.044 | 18.8343
BLD6PST |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_HEATCOIL | 5.4215 | 7.2812 | 5.8202 | 8.3646 | 4.3943 | 6.729 | 4.8381 | 9.1226 | 7.4558 | 7.0666 | 12.1812 | 9.8544 | 13.4292 | 12.6633 | 14.0441 | 18.8343
BLD6PST |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_HEATCOIL | 5.4277 | 7.2938 | 5.7983 | 8.3617 | 4.3902 | 6.7078 | 4.8292 | 9.1182 | 7.4627 | 7.0689 | 12.176 | 9.836 | 13.4346 | 12.6728 | 14.0479 | 18.836
BLD6PST |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_HEATCOIL | 5.4279 | 7.2938 | 5.7981 | 8.3617 | 4.3901 | 6.7081 | 4.8291 | 9.1183 | 7.4627 | 7.0689 | 12.1761 | 9.8358 | 13.4347 | 12.673 | 14.048 | 18.836
BLD6PST |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_HEATCOIL | 7.3833 | 11.0097 | 8.421 | 12.7718 | 7.3504 | 9.8587 | 8.3704 | 14.0602 | 11.5795 | 11.1999 | 18.2201 | 14.9683 | 20.1258 | 19.1772 | 20.9568 | 27.9019
BLD6PST |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_HEATCOIL | 7.3829 | 11.0115 | 8.433 | 12.7866 | 7.3571 | 9.8703 | 8.3818 | 14.0719 | 11.5871 | 11.2097 | 18.2337 | 14.9865 | 20.1383 | 19.1853 | 20.9709 | 27.9128
BLD6PST |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_HEATCOIL | 7.3828 | 11.0097 | 8.4164 | 12.7693 | 7.3484 | 9.862 | 8.3691 | 14.0609 | 11.5795 | 11.1998 | 18.2182 | 14.9652 | 20.1267 | 19.182 | 20.9567 | 27.9019
BLD6PST |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_HEATCOIL | 3.5355 | 5.3019 | 4.5476 | 6.1713 | 3.425 | 5.2889 | 3.8084 | 6.7829 | 5.7434 | 5.359 | 8.9285 | 7.4036 | 9.8648 | 9.3956 | 10.3337 | 13.9143
BLD6PST |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_HEATCOIL | 7.3824 | 11.0115 | 8.4283 | 12.7841 | 7.3551 | 9.8735 | 8.3806 | 14.0726 | 11.5871 | 11.2096 | 18.2318 | 14.9833 | 20.1393 | 19.1901 | 20.9708 | 27.9128
BLD6PST |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_HEATCOIL | 5.8803 | 9.1745 | 6.8768 | 10.7273 | 6.1297 | 8.1358 | 7.0875 | 11.8902 | 9.7156 | 9.4529 | 15.3906 | 12.6143 | 17.0483 | 16.2315 | 17.746 | 23.6708
BLD6PST |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_HEATCOIL | 5.8803 | 9.1745 | 6.8767 | 10.7273 | 6.1296 | 8.1358 | 7.0875 | 11.8902 | 9.7156 | 9.4529 | 15.3906 | 12.6142 | 17.0483 | 16.2316 | 17.746 | 23.6708
BLD6PST |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_HEATCOIL | 5.8765 | 9.1731 | 6.8639 | 10.713 | 6.1227 | 8.1241 | 7.0764 | 11.8795 | 9.7089 | 9.4439 | 15.3783 | 12.5974 | 17.0373 | 16.2251 | 17.7336 | 23.6619
BLD6PST |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_HEATCOIL | 5.8765 | 9.1731 | 6.8638 | 10.713 | 6.1226 | 8.1242 | 7.0764 | 11.8795 | 9.7089 | 9.4439 | 15.3783 | 12.5973 | 17.0373 | 16.2252 | 17.7336 | 23.6619
BLD6PST |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_HEATCOIL | 4.4332 | 6.6875 | 5.9475 | 7.4941 | 4.3195 | 6.7395 | 4.7693 | 7.983 | 7.1018 | 6.6743 | 9.9845 | 8.6058 | 10.8024 | 10.4448 | 11.23 | 14.5074
BLD6PST |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_HEATCOIL | 3.5422 | 5.3019 | 4.5434 | 6.1742 | 3.4229 | 5.2936 | 3.8072 | 6.7858 | 5.7434 | 5.3563 | 8.9322 | 7.3997 | 9.8688 | 9.399 | 10.3378 | 13.9143
BLD6PST |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_HEATCOIL | 2.1447 | 3.5559 | 3.0759 | 4.2101 | 2.2565 | 3.6448 | 2.5702 | 4.6879 | 3.9584 | 3.6774 | 6.1964 | 5.1269 | 6.8796 | 6.5399 | 7.2175 | 9.7699
BLD6PST |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_HEATCOIL | 2.1448 | 3.5559 | 3.0758 | 4.2101 | 2.2564 | 3.6449 | 2.5702 | 4.688 | 3.9584 | 3.6774 | 6.1964 | 5.1268 | 6.8797 | 6.54 | 7.2176 | 9.7699
BLD6PST |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_HEATCOIL | 2.1741 | 3.5766 | 3.0807 | 4.2272 | 2.2662 | 3.6476 | 2.5758 | 4.698 | 3.974 | 3.6905 | 6.2085 | 5.1317 | 6.897 | 6.557 | 7.2347 | 9.7823
BLD6PST |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_HEATCOIL | 2.2278 | 3.6846 | 3.1858 | 4.3398 | 2.3244 | 3.7608 | 2.6456 | 4.8103 | 4.0875 | 3.7987 | 6.3247 | 5.2474 | 7.0136 | 6.675 | 7.3517 | 9.9032
BLD6PST |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_HEATCOIL | 8.4744 | 10.986 | 8.9327 | 12.4906 | 6.8896 | 10.1868 | 7.4453 | 13.4841 | 11.2123 | 10.5923 | 17.8525 | 14.5816 | 19.6023 | 18.5797 | 20.4801 | 27.3142
BLD6PST |  |  | HVAC Efficiency
BLD6PST |  |  | Air Conditioning (COP)
BLD6PST | COP |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_COOLCOIL | 3.1 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.1 | 3.13 | 3.1 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.1 | 3.13 | 3.1 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.1 | 3.13 | 3.1 | 3.1
BLD6PST |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.1 | 3.13 | 3.1 | 3.1
BLD6PST |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_COOLCOIL | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_COOLCOIL | 3.1 | 3.13 | 3.1 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13 | 3.13
BLD6PST |  |  | Heating Efficiency (%)
BLD6PST |  |  | T CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6PST |  |  | G CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6PST |  |  | M CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6PST | EffHeat |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6PST |  |  | HVAC Control
BLD6PST |  |  | Economizer | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
BLD6PST | Fan |  | Fan Max Flow Rate (m3/s ) | 10.22 | 7.55 | 9.38 | 8.28 | 6.39 | 8.23 | 5.74 | 8.56 | 8.66 | 7.13 | 11.36 | 11.16 | 12.56 | 13.52 | 13.43 | 17.47
BLD6PST |  |  | T CORRIDOR UNIT HEATERFAN | 0 | 0.05 | 0 | 0.08 | 0 | 0.03 | 0 | 0.1 | 0.08 | 0.05 | 0.18 | 0.15 | 0.22 | 0.23 | 0.24 | 0.35
BLD6PST |  |  | G CORRIDOR UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | M CORRIDOR UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_FAN | 0.35 | 0.2 | 0.27 | 0.22 | 0.2 | 0.21 | 0.13 | 0.23 | 0.24 | 0.18 | 0.31 | 0.31 | 0.34 | 0.37 | 0.36 | 0.48
BLD6PST |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_FAN | 0.87 | 0.49 | 0.7 | 0.44 | 0.43 | 0.57 | 0.3 | 0.45 | 0.46 | 0.35 | 0.61 | 0.6 | 0.67 | 0.72 | 0.72 | 0.93
BLD6PST |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_FAN | 0.59 | 0.38 | 0.58 | 0.44 | 0.4 | 0.48 | 0.36 | 0.45 | 0.46 | 0.38 | 0.61 | 0.6 | 0.67 | 0.72 | 0.72 | 0.93
BLD6PST |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_FAN | 0.6 | 0.38 | 0.52 | 0.44 | 0.28 | 0.43 | 0.25 | 0.45 | 0.46 | 0.35 | 0.61 | 0.6 | 0.67 | 0.72 | 0.72 | 0.93
BLD6PST |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_FAN | 0.43 | 0.29 | 0.39 | 0.27 | 0.19 | 0.33 | 0.15 | 0.26 | 0.26 | 0.2 | 0.36 | 0.35 | 0.39 | 0.42 | 0.42 | 0.55
BLD6PST |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_FAN | 0.42 | 0.28 | 0.39 | 0.26 | 0.19 | 0.33 | 0.15 | 0.26 | 0.26 | 0.2 | 0.36 | 0.35 | 0.39 | 0.42 | 0.42 | 0.55
BLD6PST |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_FAN | 0.35 | 0.26 | 0.41 | 0.26 | 0.31 | 0.35 | 0.32 | 0.26 | 0.26 | 0.3 | 0.36 | 0.35 | 0.39 | 0.42 | 0.42 | 0.55
BLD6PST |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_FAN | 0.35 | 0.26 | 0.41 | 0.26 | 0.31 | 0.35 | 0.32 | 0.26 | 0.26 | 0.31 | 0.36 | 0.35 | 0.39 | 0.42 | 0.42 | 0.55
BLD6PST |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_FAN | 0.72 | 0.52 | 0.66 | 0.52 | 0.49 | 0.57 | 0.36 | 0.55 | 0.55 | 0.44 | 0.72 | 0.71 | 0.8 | 0.86 | 0.85 | 1.09
BLD6PST |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_FAN | 0.6 | 0.43 | 0.51 | 0.52 | 0.34 | 0.44 | 0.33 | 0.55 | 0.55 | 0.44 | 0.72 | 0.71 | 0.8 | 0.86 | 0.85 | 1.1
BLD6PST |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_FAN | 0.4 | 0.43 | 0.44 | 0.52 | 0.31 | 0.42 | 0.33 | 0.55 | 0.55 | 0.44 | 0.72 | 0.71 | 0.8 | 0.86 | 0.85 | 1.09
BLD6PST |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_FAN | 0.39 | 0.21 | 0.27 | 0.22 | 0.17 | 0.21 | 0.13 | 0.23 | 0.24 | 0.18 | 0.31 | 0.3 | 0.34 | 0.36 | 0.36 | 0.48
BLD6PST |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_FAN | 0.42 | 0.43 | 0.41 | 0.52 | 0.29 | 0.42 | 0.33 | 0.55 | 0.55 | 0.44 | 0.72 | 0.71 | 0.8 | 0.86 | 0.85 | 1.1
BLD6PST |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_FAN | 0.37 | 0.35 | 0.34 | 0.42 | 0.24 | 0.33 | 0.27 | 0.45 | 0.45 | 0.36 | 0.59 | 0.58 | 0.66 | 0.71 | 0.7 | 0.91
BLD6PST |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_FAN | 0.36 | 0.35 | 0.34 | 0.42 | 0.24 | 0.33 | 0.27 | 0.45 | 0.45 | 0.36 | 0.59 | 0.58 | 0.66 | 0.71 | 0.7 | 0.91
BLD6PST |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_FAN | 0.32 | 0.35 | 0.36 | 0.42 | 0.27 | 0.33 | 0.27 | 0.45 | 0.45 | 0.36 | 0.59 | 0.58 | 0.66 | 0.71 | 0.7 | 0.91
BLD6PST |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_FAN | 0.32 | 0.35 | 0.36 | 0.42 | 0.27 | 0.33 | 0.27 | 0.45 | 0.45 | 0.36 | 0.59 | 0.58 | 0.66 | 0.71 | 0.7 | 0.91
BLD6PST |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_FAN | 0.42 | 0.31 | 0.38 | 0.31 | 0.3 | 0.33 | 0.23 | 0.32 | 0.34 | 0.27 | 0.4 | 0.41 | 0.43 | 0.47 | 0.46 | 0.57
BLD6PST |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_FAN | 0.27 | 0.18 | 0.19 | 0.22 | 0.12 | 0.2 | 0.13 | 0.23 | 0.24 | 0.18 | 0.31 | 0.3 | 0.34 | 0.36 | 0.36 | 0.48
BLD6PST |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_FAN | 0.18 | 0.11 | 0.13 | 0.13 | 0.07 | 0.12 | 0.07 | 0.13 | 0.14 | 0.11 | 0.18 | 0.18 | 0.2 | 0.22 | 0.22 | 0.29
BLD6PST |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_FAN | 0.18 | 0.11 | 0.13 | 0.13 | 0.07 | 0.12 | 0.07 | 0.13 | 0.14 | 0.11 | 0.18 | 0.18 | 0.2 | 0.22 | 0.22 | 0.29
BLD6PST |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_FAN | 0.15 | 0.1 | 0.14 | 0.13 | 0.12 | 0.12 | 0.07 | 0.13 | 0.14 | 0.11 | 0.18 | 0.18 | 0.2 | 0.22 | 0.22 | 0.29
BLD6PST |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_FAN | 0.15 | 0.11 | 0.15 | 0.13 | 0.13 | 0.13 | 0.08 | 0.14 | 0.15 | 0.11 | 0.19 | 0.19 | 0.21 | 0.23 | 0.23 | 0.3
BLD6PST |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_FAN | 1.01 | 0.62 | 0.9 | 0.58 | 0.65 | 0.75 | 0.55 | 0.53 | 0.53 | 0.54 | 0.61 | 0.6 | 0.67 | 0.72 | 0.72 | 0.93
BLD6PST |  | Utility Costs
BLD6PST |  |  | Electric Utility Rates
BLD6PST |  |  | Average Annual Rate ($/kWh) | 0.081235 | 0.1195 | 0.10087 | 0.10403 | 0.12862 | 0.09662 | 0.14769 | 0.072717 | 0.03764 | 0.072349 | 0.052817 | 0.037681 | 0.058154 | 0.072583 | 0.056331 | 0.093062
BLD6PST |  |  | Total Cost ($/m2) | 11.16 | 12.85 | 12.23 | 9.51 | 10.29 | 10.11 | 10.85 | 6.35 | 3.25 | 5.48 | 4.48 | 3.07 | 4.97 | 5.85 | 4.61 | 8.07
BLD6PST |  |  | Gas Utility Rates
BLD6PST |  |  | Average Annual Rate ($/MJ) | 0.011435 | 0.0080948 | 0.0082667 | 0.0098116 | 0.0085579 | 0.0077468 | 0.0085354 | 0.00974 | 0.0069442 | 0.0083954 | 0.0084276 | 0.0069678 | 0.0078829 | 0.0082174 | 0.0078782 | 0.0041372
BLD6PST |  |  | Total Cost ($/m2) | 0.75 | 1.57 | 1.28 | 3.13 | 1.4 | 1.79 | 2.57 | 4.57 | 2.47 | 3.93 | 5.01 | 3.25 | 5.64 | 5.11 | 6.76 | 5.29
BLD6PST |  |  | Total Utility Costs
BLD6PST |  |  | Cost Intensity ($/m2) | 11.91 | 14.43 | 13.51 | 12.64 | 11.69 | 11.89 | 13.42 | 10.92 | 5.72 | 9.42 | 9.49 | 6.32 | 10.6 | 10.96 | 11.37 | 13.36
BLD6PST |  | Energy - End Uses
BLD6PST |  |  | Electricity (kWh)
BLD6PST |  |  | Heating | 0 | 86.1111 | 0 | 305.5556 | 0 | 5.5556 | 0 | 672.2222 | 127.7778 | 44.4444 | 1588.8889 | 733.3333 | 3455.5556 | 1969.4444 | 4427.7778 | 11302.7778
BLD6PST |  |  | Cooling | 181630.5556 | 99202.7778 | 136947.2222 | 52277.7778 | 25300 | 89152.7778 | 5058.3333 | 37647.2222 | 35113.8889 | 6827.7778 | 26275 | 19072.2222 | 23041.6667 | 11505.5556 | 8438.8889 | 5194.4444
BLD6PST |  |  | Interior Lighting | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889 | 63638.8889
BLD6PST |  |  | Exterior Lighting | 28130.5556 | 28122.2222 | 28116.6667 | 28111.1111 | 28088.8889 | 28083.3333 | 28097.2222 | 28080.5556 | 28091.6667 | 28036.1111 | 28086.1111 | 28069.4444 | 28066.6667 | 28061.1111 | 28044.4444 | 27872.2222
BLD6PST |  |  | Interior Equipment | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500
BLD6PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Fans | 32661.1111 | 21602.7778 | 26950 | 17808.3333 | 9222.2222 | 22580.5556 | 8888.8889 | 19291.6667 | 19044.4444 | 14547.2222 | 21836.1111 | 19672.2222 | 25005.5556 | 23133.3333 | 27327.7778 | 39350
BLD6PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Total End Uses | 430561.1111 | 337152.7778 | 380152.7778 | 286641.6667 | 250750 | 327961.1111 | 230186.1111 | 273830.5556 | 270519.4444 | 237591.6667 | 265925 | 255683.3333 | 267708.3333 | 252808.3333 | 256377.7778 | 271861.1111
BLD6PST |  |  | Gas (MJ)
BLD6PST |  |  | Heating | 38860 | 398840 | 300960 | 747130 | 269550 | 507200 | 666070 | 1184650 | 837970 | 1166490 | 1550920 | 1149480 | 1902640 | 1605630 | 2310560 | 3579390
BLD6PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Water Systems | 166570 | 209980 | 185050 | 251800 | 243660 | 215100 | 279450 | 284660 | 278430 | 301760 | 313510 | 312000 | 338430 | 342960 | 379550 | 429320
BLD6PST |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Total End Uses | 205440 | 608830 | 486010 | 998920 | 513220 | 722310 | 945520 | 1469310 | 1116400 | 1468240 | 1864430 | 1461490 | 2241080 | 1948590 | 2690110 | 4008710
BLD6PST |  |  | Total Building (MJ) | 1755460 | 1822570 | 1854560 | 2030840 | 1415920 | 1902960 | 1774180 | 2455100 | 2090260 | 2323580 | 2821760 | 2381950 | 3204830 | 2858700 | 3613070 | 4987410
BLD6PST |  | Energy - End Use Intensities
BLD6PST |  |  | Electricity (MJ/m2)
BLD6PST |  |  | Heating (elec) | 0 | 0.098897 | 0 | 0.35092 | 0 | 0.0063804 | 0 | 0.77203 | 0.14675 | 0.051043 | 1.8248 | 0.84222 | 3.9686 | 2.2619 | 5.0852 | 12.981
BLD6PST |  |  | Cooling (elec) | 208.5983 | 113.932 | 157.2805 | 60.0398 | 29.0564 | 102.3898 | 5.8094 | 43.2369 | 40.3274 | 7.8415 | 30.1762 | 21.904 | 26.4628 | 13.2138 | 9.6919 | 5.9657
BLD6PST |  |  | Interior Lighting (elec) | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877 | 73.0877
BLD6PST |  |  | Exterior Lighting (elec) | 32.3073 | 32.2977 | 32.2913 | 32.2849 | 32.2594 | 32.253 | 32.269 | 32.2498 | 32.2626 | 32.1988 | 32.2562 | 32.2371 | 32.2339 | 32.2275 | 32.2084 | 32.0106
BLD6PST |  |  | Interior Equipment (elec) | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852
BLD6PST |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Fans (elec) | 37.5105 | 24.8103 | 30.9514 | 20.4524 | 10.5915 | 25.9332 | 10.2087 | 22.156 | 21.8721 | 16.7071 | 25.0782 | 22.5931 | 28.7183 | 26.5681 | 31.3853 | 45.1925
BLD6PST |  |  | Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Total End Uses | 494.4889 | 387.2117 | 436.5962 | 329.2009 | 287.9802 | 376.6553 | 264.3631 | 314.4877 | 310.685 | 272.8682 | 305.4084 | 293.6461 | 307.4565 | 290.3442 | 294.4436 | 312.2258
BLD6PST |  |  | Gas (MJ/m2)
BLD6PST |  |  | Heating (gas) | 12.3972 | 127.2383 | 96.0126 | 238.3502 | 85.9921 | 161.8074 | 212.4903 | 377.9282 | 267.33 | 372.1348 | 494.776 | 366.7082 | 606.9821 | 512.2297 | 737.1171 | 1141.9005
BLD6PST |  |  | Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Water Systems (gas) | 53.1393 | 66.988 | 59.0348 | 80.3295 | 77.7327 | 68.6214 | 89.1504 | 90.8125 | 88.825 | 96.2678 | 100.0163 | 99.5345 | 107.9663 | 109.4114 | 121.0844 | 136.9621
BLD6PST |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Total End Uses | 65.5397 | 194.2295 | 155.0474 | 318.6764 | 163.728 | 230.4321 | 301.6407 | 468.7407 | 356.155 | 468.3994 | 594.7923 | 466.246 | 714.9516 | 621.6411 | 858.2016 | 1278.8626
BLD6PST |  |  | Total Building (MJ/m2) | 560.0286 | 581.4381 | 591.6436 | 647.8806 | 451.7082 | 607.0842 | 566.0007 | 783.2284 | 666.8368 | 741.2708 | 900.2007 | 759.892 | 1022.408 | 911.9853 | 1152.6452 | 1591.0885
BLD6PST |  | Peak Energy Demand
BLD6PST |  |  | Electricity Peak Demand (kW)
BLD6PST |  |  | Jan | 71.91 | 54.1809 | 49.7661 | 48.9524 | 47.4906 | 45.8189 | 44.138 | 50.7864 | 45.4991 | 45.3804 | 52.4663 | 50.5963 | 54.4957 | 53.8491 | 55.3071 | 63.0187
BLD6PST |  |  | Feb | 76.7005 | 54.6678 | 53.6982 | 47.3214 | 44.982 | 44.2213 | 43.9734 | 46.2291 | 45.1597 | 44.9489 | 48.712 | 49.8113 | 52.7029 | 51.659 | 55.1612 | 62.0662
BLD6PST |  |  | Mar | 87.6819 | 69.0841 | 72.4874 | 49.0328 | 46.8574 | 45.8338 | 42.916 | 43.7839 | 43.8732 | 44.6247 | 46.4717 | 46.7202 | 48.8813 | 47.9968 | 49.7865 | 52.4736
BLD6PST |  |  | Apr | 94.0512 | 76.8355 | 77.7799 | 63.3491 | 58.7032 | 70.1004 | 42.0821 | 48.7239 | 54.1605 | 43.4584 | 43.9029 | 47.9889 | 43.5403 | 43.0213 | 44.0689 | 47.9325
BLD6PST |  |  | May | 97.9644 | 92.2373 | 109.3991 | 77.5491 | 55.2253 | 84.6693 | 41.6453 | 61.4224 | 66.3945 | 46.7089 | 62.0732 | 57.1394 | 79.1139 | 43.7349 | 43.1615 | 41.9524
BLD6PST |  |  | Jun | 112.318 | 93.7834 | 128.9612 | 86.4087 | 55.7598 | 108.9976 | 47.662 | 93.2438 | 75.8722 | 56.1049 | 73.8773 | 65.3601 | 81.1741 | 69.5846 | 61.461 | 56.5715
BLD6PST |  |  | Jul | 108.8484 | 97.565 | 128.0256 | 99.1451 | 63.1672 | 107.8895 | 69.7653 | 91.4845 | 81.4555 | 64.5356 | 87.4937 | 71.8816 | 82.4553 | 72.9725 | 74.4019 | 62.357
BLD6PST |  |  | Aug | 111.9177 | 97.9008 | 128.041 | 86.597 | 68.459 | 104.6868 | 46.6831 | 93.3005 | 80.1533 | 62.1048 | 85.2027 | 70.7991 | 80.3878 | 67.5451 | 69.2901 | 53.7588
BLD6PST |  |  | Sep | 102.3221 | 87.9166 | 114.748 | 73.051 | 68.5388 | 95.1473 | 69.1953 | 70.5985 | 67.1762 | 77.8213 | 62.0721 | 63.3735 | 58.0815 | 56.9542 | 48.8287 | 43.5026
BLD6PST |  |  | Oct | 99.1287 | 76.2013 | 79.879 | 62.7023 | 55.4047 | 72.0621 | 48.6368 | 57.7612 | 59.0919 | 43.844 | 50.647 | 51.6849 | 51.556 | 44.7379 | 45.2431 | 50.4496
BLD6PST |  |  | Nov | 79.8658 | 63.6628 | 61.8354 | 44.8197 | 44.8102 | 43.4788 | 42.8267 | 48.4906 | 45.2421 | 45.3363 | 47.0651 | 46.391 | 48.3007 | 46.3996 | 51.2672 | 55.7546
BLD6PST |  |  | Dec | 69.1655 | 56.8523 | 45.9411 | 46.2665 | 44.3029 | 44.4248 | 43.5677 | 47.2715 | 46.7978 | 45.5923 | 53.3588 | 51.1561 | 54.5388 | 54.2387 | 54.7853 | 61.2816
BLD6PST |  |  | Time of Peak Electrical Demand
BLD6PST |  |  | Jan | 23-JAN-16:10 | 22-JAN-18:10 | 28-JAN-18:10 | 13-JAN-18:00 | 25-JAN-17:19 | 10-JAN-18:00 | 01-JAN-18:00 | 17-JAN-19:00 | 03-JAN-18:00 | 31-JAN-18:10 | 07-JAN-18:00 | 05-JAN-18:00 | 04-JAN-18:00 | 16-JAN-18:10 | 08-JAN-18:00 | 12-JAN-18:10
BLD6PST |  |  | Feb | 22-FEB-16:10 | 22-FEB-18:19 | 28-FEB-18:19 | 13-FEB-18:00 | 12-FEB-17:30 | 21-FEB-18:00 | 15-FEB-18:10 | 20-FEB-18:00 | 05-FEB-18:00 | 27-FEB-18:10 | 08-FEB-18:00 | 15-FEB-18:00 | 03-FEB-18:00 | 25-FEB-18:00 | 01-FEB-18:00 | 04-FEB-18:00
BLD6PST |  |  | Mar | 13-MAR-16:19 | 26-MAR-16:10 | 17-MAR-16:19 | 28-MAR-18:00 | 31-MAR-16:10 | 30-MAR-17:00 | 06-MAR-18:00 | 21-MAR-18:00 | 27-MAR-18:00 | 01-MAR-18:00 | 03-MAR-18:00 | 06-MAR-19:00 | 05-MAR-18:00 | 02-MAR-18:00 | 08-MAR-18:00 | 11-MAR-18:00
BLD6PST |  |  | Apr | 01-APR-16:10 | 29-APR-17:10 | 01-APR-17:10 | 15-APR-17:19 | 11-APR-17:10 | 21-APR-17:10 | 23-APR-18:00 | 05-APR-18:30 | 21-APR-17:10 | 11-APR-18:00 | 02-APR-18:19 | 26-APR-18:49 | 16-APR-18:00 | 17-APR-19:00 | 22-APR-18:00 | 01-APR-19:00
BLD6PST |  |  | May | 15-MAY-17:10 | 26-MAY-17:19 | 28-MAY-17:10 | 31-MAY-17:30 | 29-MAY-17:19 | 31-MAY-17:10 | 25-MAY-19:19 | 15-MAY-17:10 | 31-MAY-17:10 | 04-MAY-19:19 | 30-MAY-17:10 | 23-MAY-17:10 | 27-MAY-17:10 | 16-MAY-17:10 | 31-MAY-17:19 | 30-MAY-17:10
BLD6PST |  |  | Jun | 27-JUN-17:10 | 13-JUN-17:19 | 28-JUN-17:30 | 19-JUN-17:10 | 30-JUN-17:10 | 27-JUN-18:00 | 16-JUN-17:10 | 30-JUN-17:10 | 20-JUN-17:10 | 18-JUN-16:10 | 20-JUN-17:10 | 27-JUN-17:10 | 29-JUN-17:30 | 24-JUN-17:00 | 14-JUN-17:19 | 20-JUN-17:00
BLD6PST |  |  | Jul | 12-JUL-17:10 | 30-JUL-16:10 | 19-JUL-17:19 | 03-JUL-17:30 | 10-JUL-17:10 | 24-JUL-18:49 | 02-JUL-17:10 | 24-JUL-17:10 | 31-JUL-17:10 | 24-JUL-17:00 | 13-JUL-17:10 | 16-JUL-17:10 | 15-JUL-17:10 | 21-JUL-17:10 | 06-JUL-17:19 | 29-JUL-17:49
BLD6PST |  |  | Aug | 21-AUG-16:19 | 27-AUG-17:10 | 01-AUG-17:10 | 14-AUG-17:10 | 08-AUG-16:19 | 04-AUG-17:10 | 26-AUG-17:10 | 17-AUG-17:10 | 01-AUG-17:10 | 06-AUG-17:10 | 04-AUG-17:10 | 30-AUG-17:10 | 25-AUG-17:10 | 09-AUG-17:10 | 13-AUG-17:10 | 15-AUG-17:10
BLD6PST |  |  | Sep | 11-SEP-15:09 | 15-SEP-16:19 | 09-SEP-17:10 | 06-SEP-17:10 | 25-SEP-15:09 | 01-SEP-15:09 | 28-SEP-16:10 | 08-SEP-17:10 | 02-SEP-17:10 | 02-SEP-17:10 | 27-SEP-16:10 | 01-SEP-17:10 | 14-SEP-18:30 | 01-SEP-17:10 | 08-SEP-18:40 | 29-SEP-18:00
BLD6PST |  |  | Oct | 06-OCT-16:10 | 06-OCT-16:10 | 13-OCT-16:19 | 01-OCT-16:10 | 05-OCT-17:40 | 03-OCT-17:19 | 13-OCT-17:40 | 03-OCT-17:49 | 01-OCT-17:49 | 17-OCT-17:19 | 31-OCT-17:19 | 01-OCT-17:49 | 08-OCT-17:40 | 06-OCT-17:00 | 31-OCT-17:00 | 30-OCT-17:00
BLD6PST |  |  | Nov | 07-NOV-16:10 | 27-NOV-18:10 | 13-NOV-17:30 | 29-NOV-18:00 | 09-NOV-17:10 | 10-NOV-18:10 | 22-NOV-18:10 | 05-NOV-17:10 | 19-NOV-18:00 | 29-NOV-18:00 | 02-NOV-17:00 | 18-NOV-18:00 | 27-NOV-18:10 | 29-NOV-18:00 | 24-NOV-18:00 | 22-NOV-18:00
BLD6PST |  |  | Dec | 17-DEC-17:30 | 02-DEC-18:00 | 21-DEC-18:10 | 21-DEC-18:00 | 19-DEC-12:00 | 12-DEC-18:00 | 24-DEC-18:00 | 20-DEC-18:00 | 28-DEC-18:00 | 13-DEC-18:10 | 31-DEC-18:00 | 11-DEC-18:10 | 31-DEC-18:00 | 11-DEC-18:00 | 31-DEC-18:00 | 29-DEC-18:10
BLD6PST |  | Source Energy
BLD6PST |  |  | Total Source Energy (GJ) | 5365.75 | 5073.16 | 4859.45 | 4562.18 | 3354.29 | 5011.96 | 3597.23 | 5129.69 | 4450.4 | 3093.31 | 5430.66 | 4650.04 | 5759.67 | 5291.4 | 6109.81 | 7873.43
BLD6PST |  |  | Total Source Energy (MJ/m2) | 1711.79 | 1618.45 | 1550.26 | 1455.43 | 1070.09 | 1598.92 | 1147.59 | 1636.48 | 1419.77 | 986.83 | 1732.49 | 1483.46 | 1837.45 | 1688.07 | 1949.16 | 2511.79
BLD6PST |  | Water Consumption (m3)
BLD6PST |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Water Systems | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51
BLD6PST |  |  | Total Building | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51
BLD6PST |  | Emissions
BLD6PST |  |  | Carbon Equivalent (kg) | 121785.8793 | 123439.4529 | 123522.8647 | 106309.817 | 38558.8078 | 123637.8498 | 43950.9911 | 100390.6275 | 130638.1318 | 43781.243 | 175398.7878 | 130800.9434 | 132047.4708 | 127523.9304 | 136266.3551 | 148786.1563
BLD6PST |  |  | CO2 (kg) | 284126.8306 | 313915.8728 | 295199.1916 | 252441.6947 | 104975.6465 | 299619.6923 | 121081.904 | 242263.0482 | 315655.0625 | 117602.7471 | 424257.2438 | 319513.6257 | 328014.309 | 316398.3491 | 342467.6535 | 400483.1829
BLD6PST |  |  | NOX (kg) | 491.9285 | 399.7184 | 479.1259 | 434.2169 | 91.2285 | 463.8058 | 106.1851 | 400.8238 | 504.5831 | 135.4967 | 683.8397 | 496.1307 | 491.5033 | 473.5951 | 496.4265 | 429.687
BLD6PST |  |  | SO2 (kg) | 1843.0297 | 1608.3774 | 1528.7998 | 1006.3839 | 729.7898 | 1804.2361 | 670.0645 | 999.9891 | 1181.6017 | 184.0338 | 1792.6256 | 1116.9125 | 632.4357 | 675.5501 | 605.8144 | 1384.9546
BLD6PST |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6PST |  |  | Hg (kg) | 0.0084 | 0.0046 | 0.0042 | 0.0038 | 0.0004 | 0.0035 | 0.0004 | 0.0042 | 0.0047 | 0.0009 | 0.0056 | 0.0045 | 0.0049 | 0.0049 | 0.0047 | 0.0051
BLD6PST |  |  | Water for Electricity (m3) | 228.0933 | 548.5855 | 11292.2 | 1789.68 | 4402.61 | 8997.25 | 4041.53 | 62.1701 | 1228.37 | 2427.44 | 412.5677 | 1161.01 | 415.3339 | 16013.9 | 397.7553 | 277.7547
BLD6NEW |  | Location Summary
BLD6NEW |  |  |  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
BLD6NEW |  | Program
BLD6NEW |  |  | ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
BLD6NEW |  |  | Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
BLD6NEW |  |  | Weighting Factor | 100.7576 | 428.9443 | 36.62 | 323.5531 |  | 338.096 | 102.1529 | 664.3159 | 8.5981 | 145.4843 | 439.9484 | 124.8761 | 122.8797 | 22.0747 | 12.7321 | 0
BLD6NEW |  | Fabric | [6 empty] | weighting factor is for all of 3B
BLD6NEW |  |  | Exterior walls
BLD6NEW | TypeWall |  | Construction Type | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame | SteelFrame
BLD6NEW | RvalWall |  | R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 2.7548 | 3.2051
BLD6NEW |  |  | Roof
BLD6NEW | TypeRoof |  | Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
BLD6NEW | RvalRoof |  | R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
BLD6NEW |  |  | Window
BLD6NEW | Uwindow |  | U-Factor (W / m2·K) | 5.838 | 5.838 | 5.838 | 3.808 | 3.808 | 3.808 | 5.838 | 3.808 | 3.808 | 3.808 | 3.808 | 3.808 | 3.808 | 3.808 | 3.808 | 2.672
BLD6NEW | SHGC |  | SHGC | 0.251 | 0.251 | 0.251 | 0.389 | 0.389 | 0.389 | 0.61 | 0.389 | 0.389 | 0.389 | 0.389 | 0.389 | 0.389 | 0.389 | 0.49 | 0.296
BLD6NEW |  |  | Visible transmittance | 0.11 | 0.11 | 0.11 | 0.274 | 0.274 | 0.274 | 0.474 | 0.274 | 0.274 | 0.274 | 0.274 | 0.274 | 0.274 | 0.274 | 0.378 | 0.212
BLD6NEW |  |  | Skylights/TDD
BLD6NEW |  |  | U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD6NEW |  |  | SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD6NEW |  |  | Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
BLD6NEW |  |  | Foundation
BLD6NEW |  |  | Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
BLD6NEW |  |  | Construction | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet | 4in slab w/carpet
BLD6NEW |  |  | R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
BLD6NEW |  | HVAC
BLD6NEW |  |  | HVAC Sizing
BLD6NEW | HVAC |  | Air Conditioning (kW) | 129.8738 | 134.1984 | 147.1211 | 126.47 | 91.1213 | 118.5573 | 96.5357 | 117.8185 | 89.0509 | 84.7196 | 134.6626 | 105.4876 | 147.9093 | 112.5806 | 150.5374 | 125.9769
BLD6NEW |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 3.787 | 3.9341 | 3.9219 | 3.5756 | 2.7106 | 2.9356 | 2.7518 | 3.0768 | 2.1542 | 1.9836 | 3.3963 | 2.9556 | 3.9638 | 3.2038 | 4.3464 | 3.6618
BLD6NEW |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_COOLCOIL | 9.77 | 10.0119 | 10.8674 | 9.2365 | 6.3172 | 8.5788 | 6.1883 | 8.1006 | 6.1404 | 5.506 | 8.1125 | 5.9286 | 8.1546 | 5.7852 | 7.7415 | 6.5611
BLD6NEW |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_COOLCOIL | 6.5499 | 6.8712 | 8.8249 | 6.7039 | 5.3626 | 6.8482 | 7.8645 | 6.3 | 4.7153 | 5.7946 | 6.7011 | 5.3563 | 7.7992 | 6.4266 | 8.3954 | 6.9956
BLD6NEW |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_COOLCOIL | 7.0434 | 7.1433 | 8.5936 | 6.6219 | 4.486 | 6.73 | 4.0451 | 6.0977 | 4.6258 | 3.9881 | 6.7099 | 5.2981 | 7.7925 | 5.9805 | 8.376 | 6.5186
BLD6NEW |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_COOLCOIL | 5.955 | 5.9746 | 6.9418 | 5.5219 | 4.0979 | 5.7219 | 3.1826 | 5.0894 | 4.0959 | 3.5225 | 5.1586 | 3.9422 | 5.1215 | 3.3724 | 4.9187 | 3.6529
BLD6NEW |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_COOLCOIL | 5.9077 | 5.9271 | 6.8925 | 5.4651 | 4.0087 | 5.6795 | 2.998 | 5.0438 | 4.0572 | 3.4722 | 5.1123 | 3.9049 | 5.0773 | 3.3395 | 4.8768 | 3.6529
BLD6NEW |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_COOLCOIL | 5.1296 | 5.3401 | 6.5024 | 5.5063 | 4.5461 | 5.6079 | 6.8105 | 5.2658 | 4.1087 | 4.8763 | 5.3799 | 4.1092 | 5.5725 | 3.991 | 5.4171 | 3.7938
BLD6NEW |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_COOLCOIL | 5.0823 | 5.2926 | 6.4582 | 5.4574 | 4.46 | 5.563 | 6.8146 | 5.2198 | 4.0699 | 4.8868 | 5.3314 | 4.0715 | 5.5282 | 3.9596 | 5.3746 | 3.7933
BLD6NEW |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_COOLCOIL | 9.0975 | 9.469 | 9.8705 | 8.8215 | 6.158 | 8.122 | 6.9436 | 8.3202 | 5.8191 | 5.7668 | 8.1822 | 5.6336 | 8.2994 | 6.5776 | 8.1302 | 7.6264
BLD6NEW |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_COOLCOIL | 7.5104 | 7.8579 | 8.1169 | 7.2118 | 4.6883 | 6.49 | 4.0365 | 6.5793 | 4.6073 | 4.0425 | 7.8921 | 5.9389 | 8.9981 | 6.6726 | 8.765 | 7.7153
BLD6NEW |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_COOLCOIL | 5.459 | 5.8973 | 6.8509 | 5.8984 | 3.8939 | 5.448 | 4.5627 | 5.9217 | 4.4828 | 3.77 | 7.8729 | 6.2086 | 9.0125 | 6.8476 | 9.2246 | 7.7691
BLD6NEW |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_COOLCOIL | 4.0898 | 4.1168 | 3.9879 | 3.4906 | 2.4426 | 2.8245 | 1.5709 | 2.8931 | 2.1494 | 1.6276 | 3.3877 | 2.9793 | 3.9439 | 3.1815 | 4.3251 | 4.0046
BLD6NEW |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_COOLCOIL | 5.874 | 6.1379 | 6.8394 | 5.8223 | 3.6058 | 5.3824 | 2.6911 | 5.9354 | 4.4913 | 3.6772 | 7.8897 | 6.209 | 9.0289 | 6.8747 | 9.3701 | 7.7378
BLD6NEW |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_COOLCOIL | 5.3742 | 5.5818 | 6.1815 | 5.2743 | 3.4037 | 4.8828 | 2.3633 | 4.82 | 3.635 | 2.9776 | 6.402 | 5.0474 | 7.3376 | 5.6159 | 7.6623 | 6.0852
BLD6NEW |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_COOLCOIL | 5.3424 | 5.5498 | 6.1585 | 5.2419 | 3.356 | 4.8565 | 2.2809 | 4.82 | 3.6398 | 2.9825 | 6.4019 | 5.054 | 7.3377 | 5.6197 | 7.6784 | 6.0852
BLD6NEW |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_COOLCOIL | 4.8922 | 5.237 | 6.0746 | 5.2828 | 3.6421 | 4.9 | 4.0711 | 4.893 | 3.6517 | 3.4323 | 6.3865 | 5.0402 | 7.3228 | 5.6067 | 7.5442 | 6.3579
BLD6NEW |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_COOLCOIL | 4.8632 | 5.209 | 6.055 | 5.2524 | 3.6166 | 4.8776 | 4.0742 | 4.8656 | 3.6559 | 3.4142 | 6.3865 | 5.0461 | 7.3228 | 5.6102 | 7.5576 | 6.3577
BLD6NEW |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_COOLCOIL | 4.9316 | 4.9055 | 4.6471 | 4.474 | 3.4492 | 3.5888 | 3.6535 | 4.2976 | 3.0986 | 3.0711 | 5.3233 | 4.2655 | 5.7911 | 4.859 | 5.811 | 5.3745
BLD6NEW |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_COOLCOIL | 2.801 | 2.7682 | 2.6639 | 2.3618 | 1.6699 | 2.0596 | 1.489 | 2.4315 | 2.2282 | 1.641 | 3.3924 | 3.076 | 3.9503 | 3.2537 | 4.3319 | 4.2017
BLD6NEW |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_COOLCOIL | 2.3355 | 2.2699 | 1.9597 | 1.9091 | 1.6699 | 1.6699 | 1.5363 | 1.6699 | 1.4625 | 1.5504 | 2.0138 | 1.9061 | 2.377 | 1.9979 | 2.6276 | 3.1426
BLD6NEW |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_COOLCOIL | 2.3136 | 2.248 | 1.9384 | 1.8851 | 1.6699 | 1.6699 | 1.5366 | 1.6699 | 1.4647 | 1.5534 | 2.0139 | 1.9095 | 2.3771 | 2.002 | 2.6277 | 3.1426
BLD6NEW |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_COOLCOIL | 1.9566 | 1.9711 | 1.7698 | 1.9128 | 1.6699 | 1.6699 | 1.8542 | 1.7381 | 1.448 | 1.4578 | 2.0258 | 1.8783 | 2.4003 | 2.0093 | 2.6524 | 2.5878
BLD6NEW |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_COOLCOIL | 2.0299 | 2.0424 | 1.8374 | 1.9871 | 1.6699 | 1.6699 | 1.9048 | 1.8065 | 1.439 | 1.4532 | 2.1545 | 1.9834 | 2.5375 | 2.1128 | 2.795 | 2.66
BLD6NEW |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_COOLCOIL | 11.778 | 12.4417 | 13.1669 | 11.5555 | 8.5267 | 10.7805 | 11.3116 | 10.963 | 7.8103 | 8.2721 | 11.0356 | 7.7453 | 10.8626 | 7.6806 | 9.988 | 6.4982
BLD6NEW | HEAT |  | Heating (kW) | 60.7714 | 110.5184 | 84.0321 | 117.7647 | 63.7219 | 92.2588 | 79.6706 | 133.0672 | 109.439 | 103.2778 | 177.736 | 149.5417 | 202.6672 | 193.5932 | 214.8436 | 264.2636
BLD6NEW |  |  | T CORRIDOR UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.89208 | 0.43775 | 1.4832 | 1.4536 | 1.7999 | 2.7406
BLD6NEW |  |  | G CORRIDOR UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | M CORRIDOR UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 3.1976 | 2.5711 | 3.4334 | 1.7105 | 2.8335 | 2.2611 | 3.8707 | 3.2742 | 2.9907 | 5.1545 | 4.3875 | 5.8912 | 5.6421 | 6.2492 | 7.8104
BLD6NEW |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_HEATCOIL | 3.2893 | 6.6807 | 4.8164 | 6.8419 | 3.421 | 5.0578 | 4.3422 | 7.5876 | 6.1328 | 5.7592 | 10.2308 | 8.5149 | 11.6525 | 11.0278 | 12.3481 | 15.0696
BLD6NEW |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_HEATCOIL | 3.2893 | 6.6915 | 4.7956 | 6.8385 | 3.421 | 5.0502 | 4.3206 | 7.5868 | 6.1364 | 5.756 | 10.2265 | 8.4826 | 11.6677 | 11.0496 | 12.3597 | 15.0668
BLD6NEW |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_HEATCOIL | 3.2893 | 6.6807 | 4.8101 | 6.8429 | 3.421 | 5.0618 | 4.3356 | 7.5932 | 6.1328 | 5.7559 | 10.2345 | 8.5054 | 11.6617 | 11.0396 | 12.3561 | 15.0696
BLD6NEW |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_HEATCOIL | 3.2893 | 4.6802 | 3.6636 | 4.9063 | 3.421 | 3.9605 | 3.7814 | 5.5404 | 4.3677 | 4.5095 | 7.5513 | 6.1659 | 8.6354 | 8.1056 | 9.1479 | 11.3981
BLD6NEW |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_HEATCOIL | 3.2893 | 4.6802 | 3.6636 | 4.9063 | 3.421 | 3.9605 | 3.7814 | 5.5406 | 4.3677 | 4.5095 | 7.5514 | 6.1657 | 8.6356 | 8.1058 | 9.1481 | 11.3981
BLD6NEW |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_HEATCOIL | 3.2893 | 4.6918 | 3.6636 | 4.9036 | 3.421 | 3.9605 | 3.7814 | 5.5362 | 4.3735 | 4.5095 | 7.5462 | 6.1456 | 8.6446 | 8.1189 | 9.155 | 11.3998
BLD6NEW |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_HEATCOIL | 3.2893 | 4.6918 | 3.6636 | 4.9037 | 3.421 | 3.9605 | 3.7814 | 5.5363 | 4.3735 | 4.5095 | 7.5463 | 6.1454 | 8.6448 | 8.1192 | 9.1551 | 11.3998
BLD6NEW |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_HEATCOIL | 3.0276 | 5.7827 | 4.3274 | 6.2341 | 3.0753 | 4.8084 | 4.0901 | 7.0658 | 5.8859 | 5.4773 | 9.1905 | 7.8819 | 10.4044 | 10.0396 | 11.0152 | 13.3099
BLD6NEW |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_HEATCOIL | 3.033 | 5.785 | 4.3399 | 6.2481 | 3.0824 | 4.8202 | 4.1026 | 7.0784 | 5.8951 | 5.4875 | 9.2056 | 7.9026 | 10.4191 | 10.0476 | 11.0334 | 13.3253
BLD6NEW |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_HEATCOIL | 3.0275 | 5.7827 | 4.3243 | 6.2321 | 3.0748 | 4.8098 | 4.0872 | 7.0666 | 5.8859 | 5.4772 | 9.1883 | 7.8783 | 10.4058 | 10.0459 | 11.0151 | 13.3099
BLD6NEW |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 3.1806 | 2.569 | 3.4228 | 1.7105 | 2.8332 | 2.2606 | 3.8648 | 3.2648 | 2.9823 | 5.1467 | 4.3874 | 5.8735 | 5.6267 | 6.2306 | 7.8006
BLD6NEW |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_HEATCOIL | 3.0329 | 5.785 | 4.3368 | 6.2461 | 3.0819 | 4.8215 | 4.0996 | 7.0792 | 5.8951 | 5.4874 | 9.2035 | 7.899 | 10.4205 | 10.0539 | 11.0333 | 13.3253
BLD6NEW |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_HEATCOIL | 2.4649 | 4.7934 | 3.5794 | 5.2836 | 2.5869 | 4.0695 | 3.4256 | 6.0569 | 5.0143 | 4.6788 | 7.8627 | 6.732 | 8.908 | 8.5916 | 9.429 | 11.4914
BLD6NEW |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_HEATCOIL | 2.4649 | 4.7934 | 3.5793 | 5.2835 | 2.5869 | 4.0695 | 3.4256 | 6.0569 | 5.0143 | 4.6788 | 7.8627 | 6.7319 | 8.908 | 8.5917 | 9.429 | 11.4914
BLD6NEW |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_HEATCOIL | 2.4594 | 4.7915 | 3.5669 | 5.2703 | 2.5802 | 4.0584 | 3.4134 | 6.0453 | 5.006 | 4.6693 | 7.8488 | 6.7124 | 8.8947 | 8.5851 | 9.4124 | 11.4781
BLD6NEW |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_HEATCOIL | 2.4594 | 4.7915 | 3.5668 | 5.2703 | 2.5802 | 4.0584 | 3.4134 | 6.0454 | 5.006 | 4.6693 | 7.8488 | 6.7124 | 8.8947 | 8.5852 | 9.4124 | 11.4781
BLD6NEW |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_HEATCOIL | 0.97472 | 3.9783 | 3.2909 | 4.1845 | 1.7317 | 3.5601 | 2.8198 | 4.6836 | 4.0987 | 3.5698 | 6.2962 | 5.5501 | 7.028 | 6.8669 | 7.3772 | 8.6227
BLD6NEW |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 3.1806 | 2.5667 | 3.425 | 1.7105 | 2.8351 | 2.2579 | 3.8682 | 3.2648 | 2.98 | 5.1509 | 4.3831 | 5.8791 | 5.631 | 6.2365 | 7.8006
BLD6NEW |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 2.2736 | 1.8704 | 2.5408 | 1.7105 | 2.1412 | 1.8907 | 2.9234 | 2.4554 | 2.2547 | 3.9093 | 3.3048 | 4.473 | 4.2669 | 4.7451 | 6.064
BLD6NEW |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 2.2736 | 1.8704 | 2.5409 | 1.7105 | 2.1412 | 1.8907 | 2.9234 | 2.4554 | 2.2547 | 3.9094 | 3.3047 | 4.4731 | 4.2669 | 4.7452 | 6.064
BLD6NEW |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 2.2921 | 1.8736 | 2.5534 | 1.7105 | 2.1432 | 1.8907 | 2.9316 | 2.4669 | 2.2547 | 3.9201 | 3.3076 | 4.4938 | 4.2854 | 4.7668 | 6.0773
BLD6NEW |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_HEATCOIL | 1.6447 | 2.3484 | 1.9206 | 2.615 | 1.7105 | 2.1978 | 1.8907 | 3.0046 | 2.5354 | 2.2968 | 4.0361 | 3.4106 | 4.6166 | 4.4089 | 4.8917 | 6.2058
BLD6NEW |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_HEATCOIL | 3.2893 | 6.6915 | 4.8019 | 6.8375 | 3.421 | 5.0462 | 4.3273 | 7.5813 | 6.1364 | 5.7594 | 10.2229 | 8.4921 | 11.6585 | 11.0378 | 12.3517 | 15.0668
BLD6NEW |  |  | HVAC Efficiency
BLD6NEW |  |  | Air Conditioning (COP)
BLD6NEW | COP |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_COOLCOIL | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
BLD6NEW |  |  | Heating Efficiency (%)
BLD6NEW |  |  | T CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6NEW |  |  | G CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6NEW |  |  | M CORRIDOR UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
BLD6NEW | EffHeat |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
BLD6NEW |  |  | HVAC Control
BLD6NEW |  |  | Economizer | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None | None
BLD6NEW | Fan (m3/s ) |  | Fan Max Flow Rate (m3/s ) | 5.24 | 5.45 | 6.26 | 5.19 | 3.97 | 5.46 | 5.18 | 4.77 | 4.82 | 4.24 | 5.54 | 5.57 | 6.08 | 6.53 | 6.51 | 7.2
BLD6NEW |  |  | T CORRIDOR UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.02 | 0.05 | 0.06 | 0.06 | 0.09
BLD6NEW |  |  | G CORRIDOR UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | M CORRIDOR UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | SPLITSYSTEMAC:01_UNITARY_PACKAGE_FAN | 0.15 | 0.16 | 0.16 | 0.14 | 0.11 | 0.12 | 0.14 | 0.12 | 0.11 | 0.09 | 0.14 | 0.14 | 0.16 | 0.18 | 0.18 | 0.2
BLD6NEW |  |  | SPLITSYSTEMAC:10_UNITARY_PACKAGE_FAN | 0.39 | 0.4 | 0.47 | 0.37 | 0.28 | 0.4 | 0.33 | 0.33 | 0.34 | 0.28 | 0.33 | 0.32 | 0.33 | 0.34 | 0.34 | 0.38
BLD6NEW |  |  | SPLITSYSTEMAC:11_UNITARY_PACKAGE_FAN | 0.26 | 0.28 | 0.36 | 0.27 | 0.22 | 0.3 | 0.43 | 0.25 | 0.24 | 0.28 | 0.27 | 0.27 | 0.31 | 0.34 | 0.34 | 0.38
BLD6NEW |  |  | SPLITSYSTEMAC:12_UNITARY_PACKAGE_FAN | 0.28 | 0.29 | 0.35 | 0.27 | 0.18 | 0.3 | 0.21 | 0.25 | 0.24 | 0.2 | 0.27 | 0.27 | 0.31 | 0.34 | 0.34 | 0.38
BLD6NEW |  |  | SPLITSYSTEMAC:13_UNITARY_PACKAGE_FAN | 0.24 | 0.24 | 0.28 | 0.22 | 0.17 | 0.25 | 0.16 | 0.2 | 0.21 | 0.17 | 0.21 | 0.2 | 0.21 | 0.2 | 0.2 | 0.22
BLD6NEW |  |  | SPLITSYSTEMAC:14_UNITARY_PACKAGE_FAN | 0.24 | 0.24 | 0.28 | 0.22 | 0.16 | 0.24 | 0.16 | 0.2 | 0.21 | 0.17 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.22
BLD6NEW |  |  | SPLITSYSTEMAC:15_UNITARY_PACKAGE_FAN | 0.21 | 0.22 | 0.26 | 0.22 | 0.19 | 0.24 | 0.36 | 0.21 | 0.21 | 0.23 | 0.22 | 0.21 | 0.22 | 0.23 | 0.22 | 0.22
BLD6NEW |  |  | SPLITSYSTEMAC:16_UNITARY_PACKAGE_FAN | 0.2 | 0.21 | 0.26 | 0.22 | 0.18 | 0.24 | 0.37 | 0.21 | 0.21 | 0.23 | 0.21 | 0.21 | 0.22 | 0.22 | 0.22 | 0.22
BLD6NEW |  |  | SPLITSYSTEMAC:17_UNITARY_PACKAGE_FAN | 0.37 | 0.4 | 0.47 | 0.39 | 0.3 | 0.42 | 0.4 | 0.35 | 0.35 | 0.32 | 0.35 | 0.33 | 0.36 | 0.4 | 0.39 | 0.45
BLD6NEW |  |  | SPLITSYSTEMAC:18_UNITARY_PACKAGE_FAN | 0.3 | 0.32 | 0.37 | 0.3 | 0.21 | 0.32 | 0.22 | 0.26 | 0.26 | 0.21 | 0.32 | 0.33 | 0.36 | 0.4 | 0.4 | 0.45
BLD6NEW |  |  | SPLITSYSTEMAC:19_UNITARY_PACKAGE_FAN | 0.22 | 0.24 | 0.29 | 0.24 | 0.17 | 0.26 | 0.25 | 0.24 | 0.25 | 0.19 | 0.32 | 0.33 | 0.36 | 0.4 | 0.39 | 0.45
BLD6NEW |  |  | SPLITSYSTEMAC:02_UNITARY_PACKAGE_FAN | 0.16 | 0.17 | 0.16 | 0.14 | 0.1 | 0.12 | 0.08 | 0.12 | 0.11 | 0.07 | 0.14 | 0.14 | 0.16 | 0.17 | 0.17 | 0.2
BLD6NEW |  |  | SPLITSYSTEMAC:20_UNITARY_PACKAGE_FAN | 0.24 | 0.25 | 0.3 | 0.23 | 0.15 | 0.26 | 0.14 | 0.24 | 0.25 | 0.19 | 0.32 | 0.33 | 0.36 | 0.4 | 0.4 | 0.45
BLD6NEW |  |  | SPLITSYSTEMAC:21_UNITARY_PACKAGE_FAN | 0.22 | 0.22 | 0.26 | 0.21 | 0.15 | 0.23 | 0.12 | 0.19 | 0.2 | 0.15 | 0.26 | 0.27 | 0.3 | 0.32 | 0.32 | 0.37
BLD6NEW |  |  | SPLITSYSTEMAC:22_UNITARY_PACKAGE_FAN | 0.22 | 0.22 | 0.26 | 0.21 | 0.14 | 0.23 | 0.12 | 0.19 | 0.2 | 0.15 | 0.26 | 0.27 | 0.3 | 0.32 | 0.32 | 0.37
BLD6NEW |  |  | SPLITSYSTEMAC:23_UNITARY_PACKAGE_FAN | 0.2 | 0.21 | 0.25 | 0.21 | 0.16 | 0.23 | 0.22 | 0.2 | 0.2 | 0.18 | 0.26 | 0.27 | 0.29 | 0.32 | 0.32 | 0.37
BLD6NEW |  |  | SPLITSYSTEMAC:24_UNITARY_PACKAGE_FAN | 0.2 | 0.21 | 0.25 | 0.21 | 0.16 | 0.23 | 0.22 | 0.2 | 0.2 | 0.17 | 0.26 | 0.27 | 0.29 | 0.32 | 0.32 | 0.37
BLD6NEW |  |  | SPLITSYSTEMAC:03_UNITARY_PACKAGE_FAN | 0.22 | 0.22 | 0.22 | 0.21 | 0.18 | 0.18 | 0.21 | 0.19 | 0.19 | 0.17 | 0.24 | 0.25 | 0.27 | 0.29 | 0.29 | 0.31
BLD6NEW |  |  | SPLITSYSTEMAC:04_UNITARY_PACKAGE_FAN | 0.11 | 0.11 | 0.11 | 0.1 | 0.07 | 0.08 | 0.07 | 0.1 | 0.11 | 0.07 | 0.14 | 0.14 | 0.16 | 0.18 | 0.17 | 0.2
BLD6NEW |  |  | SPLITSYSTEMAC:05_UNITARY_PACKAGE_FAN | 0.09 | 0.09 | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.11 | 0.13
BLD6NEW |  |  | SPLITSYSTEMAC:06_UNITARY_PACKAGE_FAN | 0.09 | 0.09 | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.11 | 0.13
BLD6NEW |  |  | SPLITSYSTEMAC:07_UNITARY_PACKAGE_FAN | 0.08 | 0.08 | 0.07 | 0.08 | 0.07 | 0.07 | 0.09 | 0.07 | 0.07 | 0.07 | 0.08 | 0.09 | 0.1 | 0.11 | 0.11 | 0.13
BLD6NEW |  |  | SPLITSYSTEMAC:08_UNITARY_PACKAGE_FAN | 0.08 | 0.08 | 0.07 | 0.08 | 0.07 | 0.07 | 0.09 | 0.07 | 0.07 | 0.07 | 0.09 | 0.09 | 0.1 | 0.11 | 0.11 | 0.13
BLD6NEW |  |  | SPLITSYSTEMAC:09_UNITARY_PACKAGE_FAN | 0.47 | 0.5 | 0.6 | 0.49 | 0.41 | 0.53 | 0.65 | 0.44 | 0.45 | 0.44 | 0.45 | 0.44 | 0.46 | 0.46 | 0.48 | 0.38
BLD6NEW |  | Utility Costs
BLD6NEW |  |  | Electric Utility Rates
BLD6NEW |  |  | Average Annual Rate ($/kWh) | 0.079123 | 0.11513 | 0.10169 | 0.10516 | 0.12758 | 0.096479 | 0.14901 | 0.071623 | 0.037736 | 0.072318 | 0.05336 | 0.03778 | 0.057738 | 0.072471 | 0.057141 | 0.093894
BLD6NEW |  |  | Total Cost ($/m2) | 8.04 | 10.4 | 9.71 | 8.47 | 9.42 | 8.34 | 10.44 | 5.47 | 2.87 | 4.92 | 3.94 | 2.72 | 4.27 | 5.1 | 4.01 | 6.55
BLD6NEW |  |  | Gas Utility Rates
BLD6NEW |  |  | Average Annual Rate ($/MJ) | 0.011445 | 0.0081364 | 0.0084271 | 0.010211 | 0.0084406 | 0.0079341 | 0.0084977 | 0.0098424 | 0.0070437 | 0.0083743 | 0.0085144 | 0.0070219 | 0.0079277 | 0.0082754 | 0.0079078 | 0.0041325
BLD6NEW |  |  | Total Cost ($/m2) | 0.6 | 0.82 | 0.66 | 1.36 | 0.69 | 0.75 | 0.98 | 1.95 | 1.07 | 1.58 | 2.25 | 1.47 | 2.72 | 2.42 | 3.27 | 2.62
BLD6NEW |  |  | Total Utility Costs
BLD6NEW |  |  | Cost Intensity ($/m2) | 8.64 | 11.22 | 10.37 | 9.83 | 10.11 | 9.09 | 11.42 | 7.42 | 3.93 | 6.5 | 6.19 | 4.19 | 6.99 | 7.53 | 7.28 | 9.17
BLD6NEW |  | Energy - End Uses
BLD6NEW |  |  | Electricity (kWh)
BLD6NEW |  |  | Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.6667 | 2.7778 | 155.5556 | 97.2222 | 269.4444 | 1219.4444
BLD6NEW |  |  | Cooling | 101216.6667 | 70986.1111 | 85047.2222 | 44402.7778 | 27666.6667 | 60180.5556 | 16388.8889 | 32611.1111 | 30425 | 10713.8889 | 24561.1111 | 19600 | 22888.8889 | 13383.3333 | 11486.1111 | 5597.2222
BLD6NEW |  |  | Interior Lighting | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444 | 48194.4444
BLD6NEW |  |  | Exterior Lighting | 23416.6667 | 23405.5556 | 23402.7778 | 23397.2222 | 23380.5556 | 23375 | 23388.8889 | 23372.2222 | 23383.3333 | 23336.1111 | 23377.7778 | 23363.8889 | 23361.1111 | 23355.5556 | 23344.4444 | 23200
BLD6NEW |  |  | Interior Equipment | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500 | 124500
BLD6NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Fans | 21072.2222 | 16175 | 18052.7778 | 11963.8889 | 7711.1111 | 14733.3333 | 7172.2222 | 10702.7778 | 11597.2222 | 6666.6667 | 10800 | 10330.5556 | 12522.2222 | 11241.6667 | 12172.2222 | 16083.3333
BLD6NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Total End Uses | 318397.2222 | 283261.1111 | 299200 | 252458.3333 | 231452.7778 | 270983.3333 | 219641.6667 | 239380.5556 | 238100 | 213413.8889 | 231450 | 225991.6667 | 231619.4444 | 220775 | 219966.6667 | 218797.2222
BLD6NEW |  |  | Gas (MJ)
BLD6NEW |  |  | Heating | 2290 | 111250 | 65590 | 173400 | 17400 | 88000 | 89930 | 342670 | 202870 | 295360 | 522210 | 350960 | 746210 | 583970 | 924830 | 1567780
BLD6NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Water Systems | 162410 | 204730 | 180430 | 245500 | 237570 | 209730 | 272460 | 277550 | 271470 | 294210 | 305670 | 304200 | 329970 | 334390 | 370060 | 418580
BLD6NEW |  |  | Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Total End Uses | 164700 | 315980 | 246020 | 418900 | 254970 | 297720 | 362390 | 620220 | 474340 | 589570 | 827890 | 655170 | 1076180 | 918360 | 1294890 | 1986360
BLD6NEW |  |  | Total Building (MJ) | 1310940 | 1335720 | 1323140 | 1327750 | 1088200 | 1273260 | 1153090 | 1481990 | 1331490 | 1357850 | 1661110 | 1468740 | 1910020 | 1713140 | 2086770 | 2774030
BLD6NEW |  | Energy - End Use Intensities
BLD6NEW |  |  | Electricity (MJ/m2)
BLD6NEW |  |  | Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.019141 | 0.0031902 | 0.17865 | 0.11166 | 0.30945 | 1.4005
BLD6NEW |  |  | Cooling (elec) | 116.2449 | 81.5258 | 97.6747 | 50.9955 | 31.7745 | 69.1159 | 18.8222 | 37.4531 | 34.9424 | 12.3046 | 28.2078 | 22.5101 | 26.2873 | 15.3704 | 13.1915 | 6.4283
BLD6NEW |  |  | Interior Lighting (elec) | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501 | 55.3501
BLD6NEW |  |  | Exterior Lighting (elec) | 26.8935 | 26.8807 | 26.8775 | 26.8711 | 26.852 | 26.8456 | 26.8616 | 26.8424 | 26.8552 | 26.801 | 26.8488 | 26.8329 | 26.8297 | 26.8233 | 26.8105 | 26.6446
BLD6NEW |  |  | Interior Equipment (elec) | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852 | 142.9852
BLD6NEW |  |  | Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Fans (elec) | 24.2009 | 18.5766 | 20.7332 | 13.7402 | 8.856 | 16.9209 | 8.2371 | 12.2919 | 13.3191 | 7.6565 | 12.4035 | 11.8644 | 14.3815 | 12.9108 | 13.9795 | 18.4713
BLD6NEW |  |  | Total End Uses | 365.6714 | 325.3185 | 343.6239 | 289.9422 | 265.8179 | 311.2177 | 252.2531 | 274.9227 | 273.452 | 245.1006 | 265.8147 | 259.5459 | 266.0093 | 253.5547 | 252.6263 | 251.2833
BLD6NEW |  |  | Gas (MJ/m2)
BLD6NEW |  |  | Heating (gas) | 0.73056 | 35.4911 | 20.9246 | 55.3182 | 5.551 | 28.0738 | 28.6896 | 109.3189 | 64.7198 | 94.226 | 166.596 | 111.9636 | 238.0567 | 186.2987 | 295.0402 | 500.1547
BLD6NEW |  |  | Water Systems (gas) | 51.8122 | 65.3132 | 57.561 | 78.3197 | 75.7898 | 66.9083 | 86.9205 | 88.5443 | 86.6046 | 93.8592 | 97.5151 | 97.0462 | 105.2674 | 106.6774 | 118.0569 | 133.5358
BLD6NEW |  |  | Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Total End Uses | 52.5428 | 100.8043 | 78.4855 | 133.6379 | 81.3408 | 94.9789 | 115.61 | 197.8632 | 151.3244 | 188.0852 | 264.1143 | 209.013 | 343.324 | 292.9761 | 413.0971 | 633.6905
BLD6NEW |  |  | Total Building (MJ/m2) | 418.2174 | 426.1227 | 422.1094 | 423.5801 | 347.1586 | 406.1967 | 367.8599 | 472.7859 | 424.7733 | 433.1826 | 529.929 | 468.5589 | 609.3365 | 546.5276 | 665.7234 | 884.9738
BLD6NEW |  | Peak Energy Demand
BLD6NEW |  |  | Electricity Peak Demand (kW)
BLD6NEW |  |  | Jan | 56.9917 | 49.9938 | 47.9332 | 43.0605 | 45.6355 | 40.9202 | 41.3839 | 41.5933 | 40.4192 | 40.1466 | 41.734 | 41.2466 | 43.0886 | 43.0511 | 43.3384 | 46.3824
BLD6NEW |  |  | Feb | 58.987 | 50.9337 | 49.8956 | 44.5192 | 45.7528 | 44.8275 | 46.6551 | 40.153 | 42.3639 | 40.0424 | 40.6795 | 41.4656 | 41.7979 | 41.7659 | 43.2138 | 45.7233
BLD6NEW |  |  | Mar | 60.1847 | 56.3994 | 58.0623 | 48.7133 | 44.9294 | 47.2394 | 42.2435 | 42.639 | 42.7712 | 42.459 | 40.235 | 43.6862 | 40.7965 | 41.2371 | 41.2528 | 41.6604
BLD6NEW |  |  | Apr | 63.3515 | 61.8651 | 61.0813 | 54.1376 | 49.6686 | 58.3739 | 45.5933 | 48.0426 | 48.991 | 41.0232 | 42.1749 | 46.8344 | 44.154 | 40.1532 | 38.9199 | 39.3427
BLD6NEW |  |  | May | 65.54 | 70.2313 | 76.9834 | 62.07 | 50.2303 | 64.5377 | 45.4464 | 53.1959 | 55.1379 | 46.7425 | 52.4524 | 50.9663 | 63.4645 | 45.349 | 45.0447 | 40.5174
BLD6NEW |  |  | Jun | 71.1523 | 71.2671 | 87.3803 | 66.4997 | 48.9182 | 77.6715 | 48.4563 | 68.1929 | 60.0934 | 48.4322 | 59.6602 | 55.7627 | 65.593 | 58.283 | 55.2211 | 47.3169
BLD6NEW |  |  | Jul | 68.4666 | 72.2234 | 86.8815 | 71.7165 | 51.3969 | 76.9837 | 58.4897 | 67.5594 | 62.6054 | 54.2623 | 67.4792 | 59.445 | 65.7984 | 60.0484 | 62.9338 | 50.4879
BLD6NEW |  |  | Aug | 70.2215 | 73.2242 | 87.0849 | 66.223 | 54.6091 | 75.5179 | 47.8866 | 69.2208 | 61.2028 | 53.0255 | 66.1737 | 58.85 | 65.1912 | 56.4503 | 60.1786 | 46.0951
BLD6NEW |  |  | Sep | 67.1089 | 67.9822 | 79.4801 | 61.1438 | 55.0005 | 70.2041 | 59.2396 | 58.3387 | 56.6827 | 59.4853 | 55.3419 | 53.6587 | 53.2059 | 51.898 | 48.8656 | 39.3481
BLD6NEW |  |  | Oct | 66.8266 | 62.345 | 64.3725 | 55.5328 | 52.2368 | 60.3052 | 50.596 | 52.6709 | 53.1052 | 44.38 | 48.3599 | 49.9438 | 50.7055 | 45.7643 | 46.775 | 41.236
BLD6NEW |  |  | Nov | 61.7556 | 54.8139 | 52.805 | 45.3529 | 46.4512 | 45.3042 | 43.4399 | 48.2284 | 42.9519 | 41.4688 | 46.2006 | 41.8276 | 40.9836 | 40.3328 | 41.695 | 43.0205
BLD6NEW |  |  | Dec | 56.8657 | 51.4449 | 44.9741 | 41.1415 | 45.1542 | 42.3444 | 40.7775 | 40.4774 | 40.3639 | 40.3916 | 42.1821 | 41.5966 | 42.7689 | 42.6171 | 43.153 | 45.6833
BLD6NEW |  |  | Time of Peak Electrical Demand
BLD6NEW |  |  | Jan | 23-JAN-18:10 | 22-JAN-18:19 | 28-JAN-18:10 | 23-JAN-18:10 | 25-JAN-18:10 | 30-JAN-18:10 | 16-JAN-18:10 | 17-JAN-18:00 | 26-JAN-18:10 | 31-JAN-18:10 | 07-JAN-18:00 | 05-JAN-18:00 | 04-JAN-18:00 | 16-JAN-18:10 | 08-JAN-18:00 | 12-JAN-18:10
BLD6NEW |  |  | Feb | 24-FEB-18:19 | 23-FEB-18:19 | 28-FEB-18:19 | 20-FEB-18:30 | 12-FEB-18:10 | 27-FEB-18:10 | 15-FEB-18:10 | 04-FEB-18:00 | 14-FEB-18:10 | 24-FEB-18:10 | 03-FEB-18:00 | 15-FEB-18:10 | 03-FEB-18:00 | 25-FEB-18:00 | 01-FEB-18:00 | 04-FEB-18:10
BLD6NEW |  |  | Mar | 13-MAR-18:30 | 26-MAR-17:10 | 17-MAR-18:40 | 28-MAR-18:00 | 04-MAR-18:19 | 30-MAR-17:00 | 01-MAR-18:10 | 09-MAR-18:00 | 02-MAR-18:10 | 29-MAR-18:30 | 03-MAR-18:00 | 30-MAR-18:19 | 01-MAR-18:00 | 30-MAR-18:49 | 08-MAR-18:00 | 11-MAR-18:00
BLD6NEW |  |  | Apr | 01-APR-18:40 | 29-APR-17:10 | 01-APR-17:10 | 15-APR-17:30 | 11-APR-18:19 | 21-APR-18:19 | 29-APR-18:00 | 05-APR-18:30 | 21-APR-18:40 | 18-APR-18:00 | 28-APR-18:40 | 25-APR-18:49 | 16-APR-18:00 | 06-APR-18:00 | 04-APR-18:40 | 01-APR-19:00
BLD6NEW |  |  | May | 15-MAY-18:00 | 26-MAY-17:30 | 28-MAY-17:10 | 14-MAY-19:30 | 29-MAY-18:00 | 31-MAY-17:10 | 25-MAY-19:19 | 15-MAY-17:10 | 31-MAY-17:10 | 04-MAY-19:19 | 30-MAY-17:10 | 23-MAY-19:19 | 27-MAY-17:10 | 25-MAY-19:00 | 31-MAY-19:49 | 24-MAY-17:00
BLD6NEW |  |  | Jun | 27-JUN-19:19 | 13-JUN-17:19 | 28-JUN-17:10 | 19-JUN-17:19 | 28-JUN-19:10 | 27-JUN-18:00 | 16-JUN-17:10 | 30-JUN-17:10 | 20-JUN-17:10 | 18-JUN-16:10 | 20-JUN-17:10 | 27-JUN-17:10 | 29-JUN-17:30 | 25-JUN-17:00 | 14-JUN-17:19 | 20-JUN-17:00
BLD6NEW |  |  | Jul | 12-JUL-17:10 | 03-JUL-17:40 | 19-JUL-17:10 | 03-JUL-17:30 | 10-JUL-17:10 | 25-JUL-18:49 | 02-JUL-17:10 | 24-JUL-19:30 | 18-JUL-19:19 | 24-JUL-17:00 | 13-JUL-17:10 | 16-JUL-17:10 | 15-JUL-17:19 | 21-JUL-17:10 | 06-JUL-17:30 | 29-JUL-17:00
BLD6NEW |  |  | Aug | 21-AUG-18:49 | 06-AUG-19:10 | 01-AUG-17:10 | 14-AUG-17:10 | 08-AUG-17:10 | 01-AUG-18:49 | 26-AUG-17:10 | 03-AUG-19:19 | 01-AUG-19:10 | 06-AUG-17:19 | 04-AUG-19:10 | 29-AUG-17:10 | 25-AUG-18:00 | 09-AUG-17:10 | 13-AUG-19:19 | 15-AUG-17:19
BLD6NEW |  |  | Sep | 09-SEP-18:30 | 15-SEP-18:30 | 09-SEP-17:10 | 10-SEP-18:49 | 25-SEP-17:49 | 01-SEP-18:10 | 28-SEP-16:10 | 08-SEP-17:10 | 02-SEP-18:30 | 02-SEP-17:10 | 27-SEP-17:40 | 01-SEP-18:40 | 14-SEP-18:30 | 02-SEP-19:10 | 08-SEP-18:40 | 09-SEP-19:40
BLD6NEW |  |  | Oct | 07-OCT-17:00 | 29-OCT-17:40 | 13-OCT-17:00 | 01-OCT-18:19 | 05-OCT-17:40 | 03-OCT-17:19 | 13-OCT-17:40 | 20-OCT-17:19 | 01-OCT-17:49 | 09-OCT-17:40 | 31-OCT-17:19 | 01-OCT-17:49 | 08-OCT-17:40 | 06-OCT-17:00 | 07-OCT-17:40 | 30-OCT-17:00
BLD6NEW |  |  | Nov | 01-NOV-17:40 | 03-NOV-17:30 | 13-NOV-17:30 | 19-NOV-18:10 | 09-NOV-18:10 | 10-NOV-18:10 | 11-NOV-18:10 | 04-NOV-17:19 | 08-NOV-18:10 | 04-NOV-17:40 | 02-NOV-17:00 | 04-NOV-17:10 | 27-NOV-18:10 | 29-NOV-18:00 | 24-NOV-18:00 | 22-NOV-18:00
BLD6NEW |  |  | Dec | 17-DEC-18:10 | 02-DEC-18:00 | 13-DEC-18:10 | 03-DEC-18:10 | 18-DEC-18:19 | 05-DEC-18:10 | 17-DEC-18:10 | 20-DEC-18:00 | 28-DEC-18:00 | 13-DEC-18:10 | 31-DEC-18:00 | 11-DEC-18:10 | 31-DEC-18:00 | 11-DEC-18:00 | 31-DEC-18:00 | 29-DEC-18:10
BLD6NEW |  | Source Energy
BLD6NEW |  |  | Total Source Energy (GJ) | 3981.91 | 4048.74 | 3675.57 | 3514.81 | 2857.28 | 3814.61 | 2842.97 | 3758.97 | 3362.02 | 1982.16 | 3858.65 | 3414.87 | 4041.08 | 3765.52 | 4135.71 | 4982.67
BLD6NEW |  |  | Total Source Energy (MJ/m2) | 1270.31 | 1291.63 | 1172.58 | 1121.3 | 911.53 | 1216.94 | 906.97 | 1199.19 | 1072.55 | 632.35 | 1230.99 | 1089.41 | 1289.19 | 1201.28 | 1319.38 | 1589.57
BLD6NEW |  | Water Consumption (m3)
BLD6NEW |  |  | Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Water Systems | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51
BLD6NEW |  |  | Total Building | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51 | 1875.51
BLD6NEW |  | Emissions
BLD6NEW |  |  | Carbon Equivalent (kg) | 90290.7002 | 100182.6555 | 94757.1896 | 85320.417 | 31646.7862 | 96764.3459 | 32203.3406 | 75782.359 | 105816.4392 | 26175.24 | 138326.4637 | 104131.6803 | 98688.5995 | 97239.5298 | 98643.2776 | 97386.3067
BLD6NEW |  |  | CO2 (kg) | 210776.6828 | 253551.7267 | 225224.8758 | 198323.6005 | 85500.1731 | 231982.9406 | 87410.9825 | 177176.9046 | 251344.8649 | 67640.3275 | 327844.2122 | 249242.325 | 238845.5897 | 235495.3956 | 241043.5356 | 257715.3513
BLD6NEW |  |  | NOX (kg) | 364.3839 | 326.5778 | 370.6394 | 360.633 | 73.8609 | 369.0801 | 75.7877 | 318.9772 | 420.0705 | 87.2136 | 557.5887 | 408.4049 | 384.437 | 376.5331 | 377.9996 | 287.1705
BLD6NEW |  |  | SO2 (kg) | 1362.917 | 1351.2366 | 1203.2041 | 886.2414 | 673.569 | 1490.6998 | 639.2258 | 874.0007 | 1039.8565 | 165.1088 | 1560.0103 | 987.0372 | 546.9498 | 589.739 | 519.5024 | 1114.299
BLD6NEW |  |  | PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLD6NEW |  |  | Hg (kg) | 0.0062 | 0.0038 | 0.0033 | 0.0033 | 0.0003 | 0.0028 | 0.0003 | 0.0036 | 0.0041 | 0.0007 | 0.0048 | 0.0039 | 0.0041 | 0.0042 | 0.0039 | 0.004
BLD6NEW |  |  | Water for Electricity (m3) | 168.6741 | 460.8978 | 8887.52 | 1576.25 | 4063.8 | 7434.13 | 3856.4 | 54.3484 | 1081.16 | 2180.39 | 359.081 | 1026.18 | 359.3453 | 13984.7 | 341.2643 | 223.541

## Picture
DOE Commercial Building Benchmark - Midrise Apartment

## Schedules
UWG | Day | Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
|  | ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
|  | INFIL_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | OFFICE_INFIL_SCH | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 17.25 | 86.25 | 4497.32
[5 empty] | Other | [24 empty] | 24 | bar: 1 to 24
SchOcc | WD | APT_OCC_SCH | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1 | 16.42 | 114.94 | 5993.3
| Sat |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
| Sun |  |  |  |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
|  | OFF_OCC_SCH | Fraction | Through 12/31 | WD, SummerDesign, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5 | 42.5 | 2216.07
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchLight | WD | APT_LIGHT_SCH | Fraction | Through 12/31 | All | 0.067 | 0.067 | 0.067 | 0.067 | 0.187 | 0.394 | 0.44 | 0.393 | 0.172 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.206 | 0.439 | 0.616 | 0.829 | 0.986 | 1 | 0.692 | 0.384 | 0.16 | 7.88 | 55.16 | 2876.2
| Sat |  |  |  |  | 0.067 | 0.067 | 0.067 | 0.067 | 0.187 | 0.394 | 0.44 | 0.393 | 0.172 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.206 | 0.439 | 0.616 | 0.829 | 0.986 | 1 | 0.692 | 0.384 | 0.16
| Sun |  |  |  |  | 0.067 | 0.067 | 0.067 | 0.067 | 0.187 | 0.394 | 0.44 | 0.393 | 0.172 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.119 | 0.206 | 0.439 | 0.616 | 0.829 | 0.986 | 1 | 0.692 | 0.384 | 0.16
|  | OFF_LIGHT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 10.7 | 53.5 | 2789.64
[5 empty] | Other | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 4.32
|  | COR_LIGHT_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
SchEquip | WD | APT_EQP_SCH | Fraction | Through 12/31 | All | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58 | 15.79 | 110.53 | 5763.35
| Sat |  |  |  |  | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
| Sun |  |  |  |  | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
|  | OFF_EQP_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 14.23 | 71.15 | 3709.96
[5 empty] | Other | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92
|  | ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
|  | WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  |  |  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  |  |  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
|  | UnitHeater_ClgSP_Sch | Temperature | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
|  | UnitHeater_HtgSP_Sch | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
SetCool | WD | APT_CLGSETP_SCH | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
| Sat |  |  |  |  | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
| Sun |  |  |  |  | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
SetHeat | WD | APT_HTGSETP_SCH | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
| Sat |  |  |  |  | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
| Sun |  |  |  |  | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
|  | OFF_HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 429.3 | 2146.5 | 111924.64
[5 empty] | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  | OFF_CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 26.7 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 650.7 | 3253.5 | 169646.79
[5 empty] | Other | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 705.6
|  | Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
|  | Apt_Operation | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Office_Operation | On/Off | Through 12/31 | WD, SummerDesign, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 45 | 2346.43
[5 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MinOA_Sched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
|  | Apartment Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
|  | Apartment Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
|  | Apartment Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | Apartment Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
|  | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
|  | SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
|  | SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SchSWH | WD | APT_DHW_SCH | Fraction | Through 12/31 | All | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29 | 12.58 | 88.06 | 4591.7
| Sat |  |  |  |  | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
| Sun |  |  |  |  | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
SchGas | WD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sat |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sun |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0